## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 17 | 25 | 14 | 11 | 50.5 | 37.2 | 50 | 88.8 | 18.3 | 1.1 | 28.9 | 230.6 | 197.1 | 197.1 | NO
1 | OK | 25 | 23 | 14 | 11 | 50.5 | 9.72 | 50 | 88.8 | 18.3 | 66.3 | 19.8 | 212 | 227 | 212 | YES
2 | OK | 23 | 24 | 14 | 11 | 50.5 | 9.37 | 50 | 88.8 | 18.3 | 67.1 | 19.5 | 212 | 227 | 212 | YES
3 | ** OPTIMAL ** | 24 | 22 | 14 | 11 | 50.5 | 9.37 | 50 | 88.8 | 18.3 | 67.1 | 19.5 | 212 | 227 | 212 | YES
4 | OK | 22 | 10 | 14 | 11 | 50.5 | 7.3 | 50 | 88.8 | 18.3 | 71.9 | 19.5 | 210.8 | 227 | 210.8 | YES
5 | OK | 10 | 11 | 14 | 11 | 50.5 | 7.03 | 50 | 88.8 | 18.3 | 72.5 | 19.3 | 210.8 | 227 | 210.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 45-011570
TR_B (available) | 57-011122
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 88.8
TR_B Baseline Loading% | 18.3
Total Scenarios Evaluated | 6
Feasible Scenarios | 5
--- Optimal Solution ---
Switch Parent Node | 24
Switch Child Node | 22
Tie Node (TR_A side) | 14
Tie Node (TR_B side) | 11
Tie Line Distance (m) | 50.5
Load Transferred (kW) | 9.37
TR_A Loading After (%) | 67.1
TR_B Loading After (%) | 19.5
Minimum Voltage (V) | 212