## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 25 | 23 | 23 | 42 | 109.2 | 9.72 | 50 | 88.8 | 48.8 | 66.3 | 60.5 | 212 | 208.4 | 208.4 | NO
1 | ** OPTIMAL ** | 25 | 19 | 9 | 38 | 43.2 | 27.48 | 50 | 88.8 | 48.8 | 23.6 | 61.7 | 223.2 | 215 | 215 | YES
| NG | 23 | 24 | 24 | 42 | 114.9 | 9.37 | 50 | 88.8 | 48.8 | 67.1 | 60.1 | 212 | 208.3 | 208.3 | NO
2 | OK | 19 | 15 | 9 | 38 | 43.2 | 27.3 | 50 | 88.8 | 48.8 | 24 | 61.5 | 223.4 | 215 | 215 | YES
| NG | 24 | 22 | 22 | 42 | 137.7 | 9.37 | 50 | 88.8 | 48.8 | 67.1 | 60.1 | 212 | 208.3 | 208.3 | NO
3 | OK | 15 | 16 | 9 | 38 | 43.2 | 24.91 | 50 | 88.8 | 48.8 | 29.5 | 61.5 | 222.1 | 215 | 215 | YES
4 | OK | 16 | 2 | 9 | 38 | 43.2 | 24.37 | 50 | 88.8 | 48.8 | 30.8 | 61.5 | 222.1 | 215 | 215 | YES
5 | OK | 2 | 3 | 9 | 38 | 43.2 | 23.36 | 50 | 88.8 | 48.8 | 33.1 | 60.3 | 222.1 | 215 | 215 | YES
6 | OK | 3 | 4 | 9 | 38 | 43.2 | 22.37 | 50 | 88.8 | 48.8 | 35.4 | 60.3 | 222.1 | 215 | 215 | YES
7 | OK | 4 | 5 | 9 | 38 | 43.2 | 21.94 | 50 | 88.8 | 48.8 | 36.3 | 60.3 | 222 | 215 | 215 | YES
8 | OK | 5 | 6 | 9 | 38 | 43.2 | 17.58 | 50 | 88.8 | 48.8 | 46.5 | 55 | 222 | 215 | 215 | YES
9 | OK | 6 | 7 | 9 | 38 | 43.2 | 13.37 | 50 | 88.8 | 48.8 | 56.6 | 50.8 | 218.3 | 215 | 215 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 45-011570
TR_B (available) | 58-015733
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 88.8
TR_B Baseline Loading% | 48.8
Total Scenarios Evaluated | 12
Feasible Scenarios | 9
--- Optimal Solution ---
Switch Parent Node | 25
Switch Child Node | 19
Tie Node (TR_A side) | 9
Tie Node (TR_B side) | 38
Tie Line Distance (m) | 43.2
Load Transferred (kW) | 27.48
TR_A Loading After (%) | 23.6
TR_B Loading After (%) | 61.7
Minimum Voltage (V) | 215