## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 37 | 27 | 27 | 0 | 86.1 | 12.08 | 50 | 89.9 | 39.3 | 61.6 | 66.2 | 217.4 | 208.7 | 208.7 | NO
1 | OK | 27 | 29 | 29 | 0 | 93.7 | 11.44 | 50 | 89.9 | 39.3 | 63 | 63.9 | 217.3 | 211.3 | 211.3 | YES
2 | OK | 29 | 49 | 49 | 0 | 120.1 | 9.91 | 50 | 89.9 | 39.3 | 66.6 | 57.5 | 217.3 | 215.3 | 215.3 | YES
3 | OK | 49 | 50 | 50 | 0 | 122.8 | 7.74 | 50 | 89.9 | 39.3 | 71.6 | 48.8 | 217.3 | 220.6 | 217.3 | YES
4 | OK | 0 | 1 | 1 | 0 | 85.1 | 8.34 | 50 | 89.9 | 39.3 | 68.4 | 72.4 | 218.6 | 212.7 | 212.7 | YES
5 | OK | 0 | 4 | 70 | 8 | 32.8 | 6.44 | 50 | 89.9 | 39.3 | 74.8 | 64.6 | 219.5 | 215.6 | 215.6 | YES
6 | OK | 1 | 22 | 22 | 0 | 87.2 | 8.34 | 50 | 89.9 | 39.3 | 68.4 | 72.4 | 218.6 | 212.7 | 212.7 | YES
7 | OK | 4 | 5 | 70 | 8 | 32.8 | 5.76 | 50 | 89.9 | 39.3 | 76.3 | 61.8 | 219.5 | 217.6 | 217.6 | YES
8 | OK | 22 | 23 | 23 | 0 | 101.8 | 8.08 | 50 | 89.9 | 39.3 | 70.8 | 71.4 | 218.5 | 213.3 | 213.3 | YES
9 | ** OPTIMAL ** | 5 | 6 | 70 | 8 | 32.8 | 5.25 | 50 | 89.9 | 39.3 | 77.5 | 59.8 | 219.5 | 218.4 | 218.4 | YES
10 | OK | 23 | 24 | 24 | 0 | 144.4 | 7.24 | 50 | 89.9 | 39.3 | 72.8 | 67.9 | 218.5 | 215.3 | 215.3 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 45-011695
TR_B (available) | 26-005519
TR_A Rated kVA | 50
TR_B Rated kVA | 30
TR_A Baseline Loading% | 89.9
TR_B Baseline Loading% | 39.3
Total Scenarios Evaluated | 11
Feasible Scenarios | 10
--- Optimal Solution ---
Switch Parent Node | 5
Switch Child Node | 6
Tie Node (TR_A side) | 70
Tie Node (TR_B side) | 8
Tie Line Distance (m) | 32.8
Load Transferred (kW) | 5.25
TR_A Loading After (%) | 77.5
TR_B Loading After (%) | 59.8
Minimum Voltage (V) | 218.4