## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 1 | 7 | 8 | 65 | 3.5 | 17.19 | 50 | 82.5 | 36.1 | 0 | 41.8 | 148655195200.3 | 198.8 | 198.8 | NO
| NG | 7 | 5 | 8 | 65 | 3.5 | 10.2 | 50 | 82.5 | 36.1 | 58.9 | 40.8 | 220.7 | 203.1 | 203.1 | NO
| NG | 5 | 6 | 8 | 65 | 3.5 | 10.18 | 50 | 82.5 | 36.1 | 58.9 | 40.8 | 220.7 | 203.1 | 203.1 | NO
| NG | 6 | 43 | 8 | 65 | 3.5 | 8.22 | 50 | 82.5 | 36.1 | 63.4 | 40.8 | 219.5 | 203.1 | 203.1 | NO
| NG | 43 | 44 | 8 | 65 | 3.5 | 7.11 | 50 | 82.5 | 36.1 | 66 | 40.8 | 218.8 | 203.1 | 203.1 | NO
| NG | 44 | 16 | 8 | 65 | 3.5 | 6.78 | 50 | 82.5 | 36.1 | 66.7 | 40.6 | 218.8 | 204.1 | 204.1 | NO
1 | OK | 16 | 18 | 8 | 65 | 3.5 | 3.05 | 50 | 82.5 | 36.1 | 75.4 | 38.3 | 218.9 | 213.3 | 213.3 | YES
2 | OK | 18 | 51 | 8 | 65 | 3.5 | 3.05 | 50 | 82.5 | 36.1 | 75.4 | 38.3 | 218.9 | 213.3 | 213.3 | YES
3 | ** OPTIMAL ** | 51 | 50 | 8 | 65 | 3.5 | 2.71 | 50 | 82.5 | 36.1 | 76.1 | 38.1 | 218.8 | 213.9 | 213.9 | YES
4 | OK | 50 | 62 | 8 | 65 | 3.5 | 1.92 | 50 | 82.5 | 36.1 | 78 | 38.1 | 218.3 | 213.9 | 213.9 | YES
5 | OK | 62 | 61 | 8 | 65 | 3.5 | 1.92 | 50 | 82.5 | 36.1 | 78 | 38.1 | 218.3 | 213.9 | 213.9 | YES
6 | OK | 61 | 15 | 8 | 65 | 3.5 | 1.92 | 50 | 82.5 | 36.1 | 78 | 38.1 | 218.3 | 213.9 | 213.9 | YES
7 | OK | 15 | 14 | 8 | 65 | 3.5 | 1.92 | 50 | 82.5 | 36.1 | 78 | 38.1 | 218.3 | 213.9 | 213.9 | YES
8 | OK | 14 | 13 | 8 | 65 | 3.5 | 1.92 | 50 | 82.5 | 36.1 | 78 | 38.1 | 218.3 | 213.9 | 213.9 | YES
9 | OK | 13 | 12 | 8 | 65 | 3.5 | 1.55 | 50 | 82.5 | 36.1 | 78.8 | 38.1 | 218.3 | 213.9 | 213.9 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 45-011767
TR_B (available) | 58-000795
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 82.5
TR_B Baseline Loading% | 36.1
Total Scenarios Evaluated | 15
Feasible Scenarios | 9
--- Optimal Solution ---
Switch Parent Node | 51
Switch Child Node | 50
Tie Node (TR_A side) | 8
Tie Node (TR_B side) | 65
Tie Line Distance (m) | 3.5
Load Transferred (kW) | 2.71
TR_A Loading After (%) | 76.1
TR_B Loading After (%) | 38.1
Minimum Voltage (V) | 213.9