## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 23 | 9 | 67 | 25 | 205 | 9.42 | 50 | 85.9 | 22.2 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | ** OPTIMAL ** | 9 | 8 | 67 | 25 | 205 | 4.73 | 50 | 85.9 | 22.2 | 67.5 | 29.5 | 212.4 | 218.4 | 212.4 | YES
2 | OK | 8 | 7 | 67 | 25 | 205 | 4.05 | 50 | 85.9 | 22.2 | 70.1 | 29.5 | 211.9 | 218.4 | 211.9 | YES
3 | OK | 7 | 0 | 67 | 25 | 205 | 2.46 | 50 | 85.9 | 22.2 | 76.3 | 28.7 | 210.8 | 218.5 | 210.8 | YES
4 | OK | 0 | 1 | 67 | 25 | 205 | 2.33 | 50 | 85.9 | 22.2 | 76.8 | 28.2 | 210.8 | 218.6 | 210.8 | YES
5 | OK | 1 | 48 | 67 | 25 | 205 | 2.21 | 50 | 85.9 | 22.2 | 77.2 | 28.2 | 210.7 | 218.6 | 210.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 45-017609
TR_B (available) | 57-011734
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 85.9
TR_B Baseline Loading% | 22.2
Total Scenarios Evaluated | 6
Feasible Scenarios | 5
--- Optimal Solution ---
Switch Parent Node | 9
Switch Child Node | 8
Tie Node (TR_A side) | 67
Tie Node (TR_B side) | 25
Tie Line Distance (m) | 205
Load Transferred (kW) | 4.73
TR_A Loading After (%) | 67.5
TR_B Loading After (%) | 29.5
Minimum Voltage (V) | 212.4