## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 23 | 9 | 65 | 15 | 14 | 9.42 | 50 | 85.9 | 8.5 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | ** OPTIMAL ** | 9 | 54 | 65 | 15 | 14 | 4.69 | 50 | 85.9 | 8.5 | 67.5 | 21.8 | 211.2 | 220.7 | 211.2 | YES
2 | OK | 54 | 58 | 65 | 15 | 14 | 3.64 | 50 | 85.9 | 8.5 | 71.6 | 18.6 | 210.9 | 223.4 | 210.9 | YES
3 | OK | 58 | 66 | 65 | 15 | 14 | 3.61 | 50 | 85.9 | 8.5 | 71.7 | 18.6 | 210.9 | 223.4 | 210.9 | YES
4 | OK | 66 | 36 | 65 | 15 | 14 | 3.24 | 50 | 85.9 | 8.5 | 73.1 | 17.2 | 210.9 | 224.2 | 210.9 | YES
5 | OK | 36 | 35 | 65 | 15 | 14 | 2.89 | 50 | 85.9 | 8.5 | 74.5 | 17.2 | 210.6 | 224.2 | 210.6 | YES
6 | OK | 35 | 22 | 65 | 15 | 14 | 2.63 | 50 | 85.9 | 8.5 | 75.5 | 16.2 | 210.6 | 224.8 | 210.6 | YES
7 | OK | 22 | 39 | 21 | 13 | 41.8 | 2.1 | 50 | 85.9 | 8.5 | 77.5 | 14.1 | 210.6 | 226 | 210.6 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 45-017609
TR_B (available) | 65-007803
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 85.9
TR_B Baseline Loading% | 8.5
Total Scenarios Evaluated | 8
Feasible Scenarios | 7
--- Optimal Solution ---
Switch Parent Node | 9
Switch Child Node | 54
Tie Node (TR_A side) | 65
Tie Node (TR_B side) | 15
Tie Line Distance (m) | 14
Load Transferred (kW) | 4.69
TR_A Loading After (%) | 67.5
TR_B Loading After (%) | 21.8
Minimum Voltage (V) | 211.2