## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 13 | 3 | 31 | 3 | 2.1 | 16.97 | 50 | 97.1 | 13.8 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 13 | 11 | 14 | 3 | 97.6 | 8.2 | 50 | 97.1 | 13.8 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 3 | 2 | 31 | 3 | 2.1 | 15.9 | 50 | 97.1 | 13.8 | 35.6 | 64.2 | 221.9 | 202.5 | 202.5 | NO
1 | ** OPTIMAL ** | 11 | 10 | 14 | 3 | 97.6 | 5.32 | 50 | 97.1 | 13.8 | 76.5 | 34.7 | 216.6 | 218.3 | 216.6 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 45-018944
TR_B (available) | 63-014772
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 97.1
TR_B Baseline Loading% | 13.8
Total Scenarios Evaluated | 4
Feasible Scenarios | 1
--- Optimal Solution ---
Switch Parent Node | 11
Switch Child Node | 10
Tie Node (TR_A side) | 14
Tie Node (TR_B side) | 3
Tie Line Distance (m) | 97.6
Load Transferred (kW) | 5.32
TR_A Loading After (%) | 76.5
TR_B Loading After (%) | 34.7
Minimum Voltage (V) | 216.6