## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 37 | 5 | 50 | 7 | 2.8 | 1.61 | 50 | 84.5 | 22.8 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 11 | 12 | 12 | 7 | 92.4 | 2.24 | 50 | 84.5 | 22.8 | 75.7 | 31.5 | 210.8 | 220.3 | 210.8 | YES
2 | OK | 11 | 36 | 36 | 7 | 87.5 | 3.69 | 50 | 84.5 | 22.8 | 70 | 37.3 | 212.2 | 217.1 | 212.2 | YES
3 | OK | 11 | 24 | 24 | 7 | 105.1 | 4.93 | 50 | 84.5 | 22.8 | 65.1 | 42.4 | 214.5 | 213.3 | 213.3 | YES
4 | OK | 12 | 16 | 18 | 7 | 112.6 | 1.8 | 50 | 84.5 | 22.8 | 77.4 | 29.8 | 210.4 | 221 | 210.4 | YES
5 | OK | 36 | 38 | 47 | 19 | 137.3 | 1.97 | 50 | 84.5 | 22.8 | 76.7 | 30.5 | 210.6 | 220.3 | 210.6 | YES
6 | ** OPTIMAL ** | 24 | 22 | 22 | 7 | 114.8 | 4.5 | 50 | 84.5 | 22.8 | 66.8 | 40.7 | 214.1 | 214.1 | 214.1 | YES
7 | OK | 38 | 39 | 47 | 19 | 137.3 | 1.72 | 50 | 84.5 | 22.8 | 77.7 | 29.5 | 210.3 | 221.2 | 210.3 | YES
8 | OK | 22 | 23 | 23 | 7 | 120.7 | 4.1 | 50 | 84.5 | 22.8 | 68.3 | 39.1 | 213.7 | 214.9 | 213.7 | YES
9 | OK | 39 | 40 | 47 | 19 | 137.3 | 1.59 | 50 | 84.5 | 22.8 | 78.2 | 29 | 210.2 | 221.6 | 210.2 | YES
10 | OK | 23 | 35 | 35 | 7 | 161.5 | 3.98 | 50 | 84.5 | 22.8 | 68.8 | 38.6 | 213.6 | 215.2 | 213.6 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 45-020017
TR_B (available) | 60-031434
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 84.5
TR_B Baseline Loading% | 22.8
Total Scenarios Evaluated | 11
Feasible Scenarios | 10
--- Optimal Solution ---
Switch Parent Node | 24
Switch Child Node | 22
Tie Node (TR_A side) | 22
Tie Node (TR_B side) | 7
Tie Line Distance (m) | 114.8
Load Transferred (kW) | 4.5
TR_A Loading After (%) | 66.8
TR_B Loading After (%) | 40.7
Minimum Voltage (V) | 214.1