## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 13 | 51 | 57 | 113 | 10.2 | 21.05 | 50 | 87.2 | 29.8 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 51 | 50 | 57 | 113 | 10.2 | 21.05 | 50 | 87.2 | 29.8 | 4.2 | 38.2 | 229.9 | 174 | 174 | NO
| NG | 50 | 49 | 57 | 113 | 10.2 | 21.05 | 50 | 87.2 | 29.8 | 6 | 38.2 | 229.9 | 173.8 | 173.8 | NO
| NG | 49 | 28 | 42 | 99 | 21.3 | 14.48 | 50 | 87.2 | 29.8 | 31.2 | 37.7 | 223.9 | 195.3 | 195.3 | NO
| NG | 49 | 8 | 57 | 113 | 10.2 | 6.05 | 50 | 87.2 | 29.8 | 63.9 | 32.7 | 219.3 | 205.4 | 205.4 | NO
| NG | 28 | 27 | 42 | 99 | 21.3 | 12.34 | 50 | 87.2 | 29.8 | 39.4 | 36.4 | 222.9 | 200.4 | 200.4 | NO
| NG | 8 | 4 | 57 | 113 | 10.2 | 5.52 | 50 | 87.2 | 29.8 | 65.9 | 32.7 | 219.2 | 205.9 | 205.9 | NO
| NG | 27 | 26 | 42 | 99 | 21.3 | 10.49 | 50 | 87.2 | 29.8 | 46.5 | 35.4 | 221.6 | 206.1 | 206.1 | NO
1 | OK | 4 | 1 | 57 | 113 | 10.2 | 2.6 | 50 | 87.2 | 29.8 | 77.2 | 31.2 | 216.9 | 214.3 | 214.3 | YES
| NG | 26 | 31 | 42 | 99 | 21.3 | 9.63 | 50 | 87.2 | 29.8 | 49.3 | 34.9 | 221.3 | 207.3 | 207.3 | NO
| NG | 31 | 29 | 42 | 99 | 21.3 | 9.27 | 50 | 87.2 | 29.8 | 51.1 | 34.7 | 221.2 | 207.6 | 207.6 | NO
| NG | 29 | 10 | 42 | 99 | 21.3 | 8.95 | 50 | 87.2 | 29.8 | 52.4 | 34.5 | 221.2 | 207.5 | 207.5 | NO
| NG | 10 | 11 | 42 | 99 | 21.3 | 6.98 | 50 | 87.2 | 29.8 | 59.9 | 33.4 | 221.2 | 207 | 207 | NO
2 | OK | 11 | 32 | 42 | 99 | 21.3 | 5.37 | 50 | 87.2 | 29.8 | 66.2 | 32.6 | 220.2 | 210.6 | 210.6 | YES
3 | OK | 32 | 18 | 42 | 99 | 21.3 | 5.24 | 50 | 87.2 | 29.8 | 66.2 | 32.5 | 220.2 | 210.6 | 210.6 | YES
4 | OK | 18 | 19 | 42 | 99 | 21.3 | 3.86 | 50 | 87.2 | 29.8 | 72 | 31.8 | 220.2 | 210.3 | 210.3 | YES
| NG | 19 | 39 | 42 | 99 | 21.3 | 3.72 | 50 | 87.2 | 29.8 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 29.8% (degenerate)
5 | OK | 39 | 16 | 44 | 57 | 41.6 | 2.52 | 50 | 87.2 | 29.8 | 77.3 | 31.1 | 219.2 | 214.3 | 214.3 | YES
6 | ** OPTIMAL ** | 16 | 17 | 44 | 57 | 41.6 | 2.37 | 50 | 87.2 | 29.8 | 77.9 | 31 | 218.9 | 214.7 | 214.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 45-023361
TR_B (available) | 38-023729
TR_A Rated kVA | 30
TR_B Rated kVA | 250
TR_A Baseline Loading% | 87.2
TR_B Baseline Loading% | 29.8
Total Scenarios Evaluated | 19
Feasible Scenarios | 6
--- Optimal Solution ---
Switch Parent Node | 16
Switch Child Node | 17
Tie Node (TR_A side) | 44
Tie Node (TR_B side) | 57
Tie Line Distance (m) | 41.6
Load Transferred (kW) | 2.37
TR_A Loading After (%) | 77.9
TR_B Loading After (%) | 31
Minimum Voltage (V) | 214.7