## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 40 | 17 | 17 | 41 | 80 | 20.85 | 50 | 72 | 33 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 40 | 39 | 45 | 29 | 43.7 | 9.88 | 50 | 72 | 33 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 17 | 12 | 12 | 41 | 86 | 20.85 | 50 | 72 | 33 | 22.7 | 51.3 | 225.5 | 166.9 | 166.9 | NO
| NG | 39 | 18 | 45 | 29 | 43.7 | 8.79 | 50 | 72 | 33 | 51.7 | 39.7 | 214.8 | 208.5 | 208.5 | NO
| NG | 12 | 11 | 11 | 41 | 119.1 | 20.57 | 50 | 72 | 33 | 23.4 | 51 | 225.5 | 169.5 | 169.5 | NO
| NG | 18 | 19 | 45 | 29 | 43.7 | 8.65 | 50 | 72 | 33 | 52 | 39.6 | 214.8 | 209.1 | 209.1 | NO
1 | ** OPTIMAL ** | 19 | 29 | 45 | 29 | 43.7 | 7.25 | 50 | 72 | 33 | 52 | 38.5 | 214.8 | 214.8 | 214.8 | YES
2 | OK | 29 | 0 | 45 | 29 | 43.7 | 6.85 | 50 | 72 | 33 | 56.1 | 38.2 | 214.6 | 214.4 | 214.4 | YES
3 | OK | 0 | 1 | 45 | 29 | 43.7 | 4.61 | 50 | 72 | 33 | 61.3 | 36.4 | 214.3 | 218.3 | 214.3 | YES
4 | OK | 0 | 30 | 28 | 42 | 56 | 2.24 | 50 | 72 | 33 | 66.8 | 34.6 | 214.6 | 217.5 | 214.6 | YES
5 | OK | 1 | 2 | 45 | 29 | 43.7 | 3.15 | 50 | 72 | 33 | 61.3 | 35.3 | 214.3 | 218 | 214.3 | YES
6 | OK | 30 | 31 | 28 | 42 | 56 | 1.97 | 50 | 72 | 33 | 67.4 | 34.4 | 214.6 | 218.6 | 214.6 | YES
7 | OK | 2 | 3 | 45 | 29 | 43.7 | 3.15 | 50 | 72 | 33 | 64.6 | 35.3 | 214.3 | 218 | 214.3 | YES
8 | OK | 31 | 32 | 28 | 42 | 56 | 1.23 | 50 | 72 | 33 | 69.1 | 33.9 | 214.6 | 219.7 | 214.6 | YES
9 | OK | 3 | 23 | 45 | 29 | 43.7 | 2.99 | 50 | 72 | 33 | 65 | 35.2 | 214.3 | 218 | 214.3 | YES
10 | OK | 32 | 33 | 28 | 42 | 56 | 0.97 | 50 | 72 | 33 | 69.7 | 33.7 | 214.6 | 219.8 | 214.6 | YES
11 | OK | 23 | 45 | 45 | 29 | 43.7 | 2.99 | 50 | 72 | 33 | 65 | 35.2 | 214.3 | 218 | 214.3 | YES
12 | OK | 33 | 27 | 28 | 42 | 56 | 0.55 | 50 | 72 | 33 | 70.7 | 33.4 | 214.6 | 219.8 | 214.6 | YES
13 | OK | 45 | 41 | 20 | 27 | 44.8 | 2.99 | 50 | 72 | 33 | 65 | 35.2 | 214.3 | 219 | 214.3 | YES
14 | OK | 41 | 21 | 20 | 27 | 44.8 | 2.11 | 50 | 72 | 33 | 67.1 | 34.5 | 214.3 | 218.9 | 214.3 | YES
15 | OK | 21 | 20 | 20 | 27 | 44.8 | 0.71 | 50 | 72 | 33 | 70.3 | 33.5 | 214.3 | 219.8 | 214.3 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 45-025032
TR_B (available) | 55-013748
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 72
TR_B Baseline Loading% | 33
Total Scenarios Evaluated | 21
Feasible Scenarios | 15
--- Optimal Solution ---
Switch Parent Node | 19
Switch Child Node | 29
Tie Node (TR_A side) | 45
Tie Node (TR_B side) | 29
Tie Line Distance (m) | 43.7
Load Transferred (kW) | 7.25
TR_A Loading After (%) | 52
TR_B Loading After (%) | 38.5
Minimum Voltage (V) | 214.8