## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 40 | 39 | 34 | 35 | 5.2 | 9.88 | 50 | 72 | 29.5 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 39 | 18 | 34 | 35 | 5.2 | 8.79 | 50 | 72 | 29.5 | 51.7 | 38.9 | 214.8 | 217.1 | 214.8 | YES
2 | OK | 18 | 19 | 34 | 35 | 5.2 | 8.65 | 50 | 72 | 29.5 | 52 | 38.7 | 214.8 | 217.5 | 214.8 | YES
3 | ** OPTIMAL ** | 19 | 29 | 34 | 35 | 5.2 | 7.25 | 50 | 72 | 29.5 | 52 | 37 | 214.8 | 220.6 | 214.8 | YES
4 | OK | 29 | 0 | 34 | 35 | 5.2 | 6.85 | 50 | 72 | 29.5 | 56.1 | 37 | 214.6 | 220.6 | 214.6 | YES
5 | OK | 0 | 1 | 34 | 35 | 5.2 | 4.61 | 50 | 72 | 29.5 | 61.3 | 34.9 | 214.3 | 221.1 | 214.3 | YES
6 | OK | 1 | 2 | 34 | 35 | 5.2 | 3.15 | 50 | 72 | 29.5 | 61.3 | 33.2 | 214.3 | 225.5 | 214.3 | YES
7 | OK | 2 | 3 | 34 | 35 | 5.2 | 3.15 | 50 | 72 | 29.5 | 64.6 | 33.2 | 214.3 | 225.5 | 214.3 | YES
8 | OK | 3 | 23 | 34 | 35 | 5.2 | 2.99 | 50 | 72 | 29.5 | 65 | 33 | 214.3 | 226 | 214.3 | YES
9 | OK | 23 | 45 | 34 | 35 | 5.2 | 2.99 | 50 | 72 | 29.5 | 65 | 33 | 214.3 | 226 | 214.3 | YES
10 | OK | 45 | 41 | 34 | 35 | 5.2 | 2.99 | 50 | 72 | 29.5 | 65 | 33 | 214.3 | 226 | 214.3 | YES
11 | OK | 41 | 21 | 34 | 35 | 5.2 | 2.11 | 50 | 72 | 29.5 | 67.1 | 32 | 214.3 | 225.9 | 214.3 | YES
12 | OK | 21 | 20 | 34 | 35 | 5.2 | 0.71 | 50 | 72 | 29.5 | 70.3 | 30.4 | 214.3 | 226.2 | 214.3 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 45-025032
TR_B (available) | 58-014090
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 72
TR_B Baseline Loading% | 29.5
Total Scenarios Evaluated | 13
Feasible Scenarios | 12
--- Optimal Solution ---
Switch Parent Node | 19
Switch Child Node | 29
Tie Node (TR_A side) | 34
Tie Node (TR_B side) | 35
Tie Line Distance (m) | 5.2
Load Transferred (kW) | 7.25
TR_A Loading After (%) | 52
TR_B Loading After (%) | 37
Minimum Voltage (V) | 214.8