## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 3 | 4 | 37 | 2 | 22 | 21.82 | 50 | 93.9 | 6.2 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 4 | 1 | 37 | 2 | 22 | 21.22 | 50 | 93.9 | 6.2 | [5 empty] | NO | TR_B sim: not converged
| NG | 1 | 8 | 37 | 2 | 22 | 12.77 | 50 | 93.9 | 6.2 | 43.8 | 61.3 | 219.7 | 190 | 190 | NO
| NG | 8 | 7 | 37 | 2 | 22 | 11.42 | 50 | 93.9 | 6.2 | 49 | 54.4 | 218.6 | 195.9 | 195.9 | NO
| NG | 7 | 5 | 37 | 2 | 22 | 10.37 | 50 | 93.9 | 6.2 | 53.1 | 49.3 | 217.6 | 199.9 | 199.9 | NO
| NG | 5 | 6 | 37 | 2 | 22 | 8.93 | 50 | 93.9 | 6.2 | 58.6 | 42.6 | 216.4 | 204.5 | 204.5 | NO
| NG | 6 | 24 | 37 | 2 | 22 | 8.93 | 50 | 93.9 | 6.2 | 58.6 | 42.6 | 216.4 | 204.5 | 204.5 | NO
| NG | 24 | 43 | 37 | 2 | 22 | 7.52 | 50 | 93.9 | 6.2 | 64.1 | 36.3 | 215.1 | 208.9 | 208.9 | NO
| NG | 43 | 32 | 37 | 2 | 22 | 7.52 | 50 | 93.9 | 6.2 | 64.1 | 36.3 | 215.1 | 208.9 | 208.9 | NO
1 | ** OPTIMAL ** | 32 | 31 | 37 | 2 | 22 | 7.52 | 50 | 93.9 | 6.2 | 64.1 | 31.2 | 215.1 | 212.4 | 212.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 45-028182
TR_B (available) | 60-022636
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 93.9
TR_B Baseline Loading% | 6.2
Total Scenarios Evaluated | 10
Feasible Scenarios | 1
--- Optimal Solution ---
Switch Parent Node | 32
Switch Child Node | 31
Tie Node (TR_A side) | 37
Tie Node (TR_B side) | 2
Tie Line Distance (m) | 22
Load Transferred (kW) | 7.52
TR_A Loading After (%) | 64.1
TR_B Loading After (%) | 31.2
Minimum Voltage (V) | 212.4