## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 4 | 1 | 41 | 6 | 40.7 | 21.22 | 50 | 93.9 | 8.9 | 11.2 | 104.9 | 228.1 | 169.4 | 169.4 | NO
1 | OK | 1 | 2 | 41 | 6 | 40.7 | 8.45 | 50 | 93.9 | 8.9 | 60.7 | 42.5 | 211.5 | 213 | 211.5 | YES
| NG | 1 | 8 | 20 | 6 | 108.7 | 12.77 | 50 | 93.9 | 8.9 | 43.8 | 63.4 | 219.7 | 191 | 191 | NO
2 | OK | 2 | 9 | 41 | 6 | 40.7 | 7.46 | 50 | 93.9 | 8.9 | 64.5 | 38.4 | 210.5 | 215 | 210.5 | YES
| NG | 8 | 7 | 20 | 6 | 108.7 | 11.42 | 50 | 93.9 | 8.9 | 49 | 56.6 | 218.6 | 196.7 | 196.7 | NO
| NG | 7 | 5 | 20 | 6 | 108.7 | 10.37 | 50 | 93.9 | 8.9 | 53.1 | 51.6 | 217.6 | 200.7 | 200.7 | NO
| NG | 5 | 6 | 20 | 6 | 108.7 | 8.93 | 50 | 93.9 | 8.9 | 58.6 | 45 | 216.4 | 205.3 | 205.3 | NO
| NG | 6 | 24 | 20 | 6 | 108.7 | 8.93 | 50 | 93.9 | 8.9 | 58.6 | 45 | 216.4 | 205.3 | 205.3 | NO
| NG | 24 | 43 | 20 | 6 | 108.7 | 7.52 | 50 | 93.9 | 8.9 | 64.1 | 38.7 | 215.1 | 209.5 | 209.5 | NO
| NG | 43 | 32 | 20 | 6 | 108.7 | 7.52 | 50 | 93.9 | 8.9 | 64.1 | 38.7 | 215.1 | 209.5 | 209.5 | NO
3 | ** OPTIMAL ** | 32 | 31 | 20 | 6 | 108.7 | 7.52 | 50 | 93.9 | 8.9 | 64.1 | 33.7 | 215.1 | 212.9 | 212.9 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 45-028182
TR_B (available) | 66-007099
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 93.9
TR_B Baseline Loading% | 8.9
Total Scenarios Evaluated | 11
Feasible Scenarios | 3
--- Optimal Solution ---
Switch Parent Node | 32
Switch Child Node | 31
Tie Node (TR_A side) | 20
Tie Node (TR_B side) | 6
Tie Line Distance (m) | 108.7
Load Transferred (kW) | 7.52
TR_A Loading After (%) | 64.1
TR_B Loading After (%) | 33.7
Minimum Voltage (V) | 212.9