## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 11 | 12 | 16 | 43 | 147.1 | 4.36 | 50 | 80 | 45.3 | 63.3 | 55.9 | 217.3 | 211.4 | 211.4 | YES
2 | OK | 12 | 13 | 16 | 43 | 147.1 | 3.95 | 50 | 80 | 45.3 | 64.8 | 54.8 | 217.3 | 213.3 | 213.3 | YES
3 | OK | 13 | 14 | 16 | 43 | 147.1 | 2.79 | 50 | 80 | 45.3 | 69.3 | 51.9 | 217.3 | 218.2 | 217.3 | YES
4 | OK | 14 | 15 | 16 | 43 | 147.1 | 1.91 | 50 | 80 | 45.3 | 72.6 | 49.8 | 217.3 | 221.7 | 217.3 | YES
5 | OK | 15 | 34 | 16 | 43 | 147.1 | 1.75 | 50 | 80 | 45.3 | 73.2 | 49.4 | 217.3 | 222.3 | 217.3 | YES
6 | OK | 34 | 17 | 16 | 43 | 147.1 | 1.63 | 50 | 80 | 45.3 | 73.7 | 49.1 | 217.3 | 222.7 | 217.3 | YES
7 | ** OPTIMAL ** | 17 | 16 | 16 | 43 | 147.1 | 0.63 | 50 | 80 | 45.3 | 77.6 | 46.8 | 217.3 | 224.1 | 217.3 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 45-028477
TR_B (available) | 49-014771
TR_A Rated kVA | 30
TR_B Rated kVA | 50
TR_A Baseline Loading% | 80
TR_B Baseline Loading% | 45.3
Total Scenarios Evaluated | 7
Feasible Scenarios | 7
--- Optimal Solution ---
Switch Parent Node | 17
Switch Child Node | 16
Tie Node (TR_A side) | 16
Tie Node (TR_B side) | 43
Tie Line Distance (m) | 147.1
Load Transferred (kW) | 0.63
TR_A Loading After (%) | 77.6
TR_B Loading After (%) | 46.8
Minimum Voltage (V) | 217.3