## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 22 | 9 | 19 | 21 | 38.2 | 38.04 | 50 | 90.6 | 24 | 1.9 | 54 | 230.5 | 196.3 | 196.3 | NO
| NG | 9 | 7 | 19 | 21 | 38.2 | 38.04 | 50 | 90.6 | 24 | 1.9 | 54 | 230.5 | 196.3 | 196.3 | NO
| NG | 7 | 6 | 19 | 21 | 38.2 | 21.98 | 50 | 90.6 | 24 | 38.9 | 40.9 | 224.2 | 206.7 | 206.7 | NO
1 | ** OPTIMAL ** | 7 | 0 | 0 | 50 | 76.8 | 16.06 | 50 | 90.6 | 24 | 53.1 | 36 | 216.2 | 217.9 | 216.2 | YES
2 | OK | 6 | 8 | 8 | 50 | 86.6 | 15.17 | 50 | 90.6 | 24 | 54.6 | 35.6 | 222.8 | 211.1 | 211.1 | YES
3 | OK | 6 | 18 | 19 | 21 | 38.2 | 6.06 | 50 | 90.6 | 24 | 76.4 | 28.4 | 212.5 | 223.3 | 212.5 | YES
4 | OK | 0 | 17 | 17 | 50 | 79.9 | 12.37 | 50 | 90.6 | 24 | 61.6 | 33.2 | 216 | 218.9 | 216 | YES
5 | OK | 8 | 5 | 5 | 50 | 90.5 | 11.99 | 50 | 90.6 | 24 | 62 | 33.1 | 221.5 | 214 | 214 | YES
6 | OK | 5 | 4 | 27 | 25 | 91.2 | 9.56 | 50 | 90.6 | 24 | 67.6 | 31.4 | 221.5 | 212.1 | 212.1 | YES
7 | OK | 4 | 27 | 27 | 25 | 91.2 | 9.12 | 50 | 90.6 | 24 | 68.6 | 31 | 221.3 | 212.7 | 212.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 45-029953
TR_B (available) | 60-011401
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 90.6
TR_B Baseline Loading% | 24
Total Scenarios Evaluated | 10
Feasible Scenarios | 7
--- Optimal Solution ---
Switch Parent Node | 7
Switch Child Node | 0
Tie Node (TR_A side) | 0
Tie Node (TR_B side) | 50
Tie Line Distance (m) | 76.8
Load Transferred (kW) | 16.06
TR_A Loading After (%) | 53.1
TR_B Loading After (%) | 36
Minimum Voltage (V) | 216.2