## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 38 | 23 | 58 | 52 | 95.9 | 9.72 | 50 | 85.6 | 36 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 38 | 13 | 42 | 66 | 8.7 | 27.26 | 50 | 85.6 | 36 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 23 | 24 | 58 | 52 | 95.9 | 9.72 | 50 | 85.6 | 36 | 63.3 | 38.7 | 220.8 | 210.6 | 210.6 | YES
| NG | 13 | 12 | 42 | 66 | 8.7 | 24.84 | 50 | 85.6 | 36 | 27.9 | 42.8 | 227.1 | 203.6 | 203.6 | NO
2 | OK | 24 | 25 | 25 | 52 | 111 | 8.84 | 50 | 85.6 | 36 | 65.3 | 38.7 | 220.8 | 210.8 | 210.8 | YES
| NG | 12 | 14 | 42 | 66 | 8.7 | 22.93 | 50 | 85.6 | 36 | 32.2 | 42.8 | 226.9 | 203.6 | 203.6 | NO
3 | OK | 25 | 26 | 26 | 52 | 133.5 | 8.44 | 50 | 85.6 | 36 | 66.2 | 38.4 | 220.8 | 212.1 | 212.1 | YES
| NG | 14 | 15 | 42 | 66 | 8.7 | 21.54 | 50 | 85.6 | 36 | 35.4 | 41.6 | 226.5 | 207 | 207 | NO
4 | OK | 26 | 27 | 59 | 66 | 148.4 | 7.3 | 50 | 85.6 | 36 | 68.8 | 38 | 220.6 | 215.3 | 215.3 | YES
| NG | 15 | 41 | 42 | 66 | 8.7 | 20.89 | 50 | 85.6 | 36 | 36.9 | 41 | 226.2 | 208.5 | 208.5 | NO
| NG | 41 | 42 | 42 | 66 | 8.7 | 18.27 | 50 | 85.6 | 36 | 42.9 | 41 | 226.2 | 208.5 | 208.5 | NO
5 | OK | 42 | 43 | 43 | 66 | 12.4 | 17.5 | 50 | 85.6 | 36 | 44.7 | 40.4 | 225.8 | 210.2 | 210.2 | YES
6 | OK | 43 | 53 | 53 | 66 | 47.6 | 9.96 | 50 | 85.6 | 36 | 62.2 | 38 | 223 | 216.7 | 216.7 | YES
7 | OK | 43 | 17 | 17 | 66 | 32 | 7.54 | 50 | 85.6 | 36 | 67.9 | 38.3 | 222.3 | 216.3 | 216.3 | YES
8 | OK | 53 | 54 | 54 | 66 | 50.3 | 8.64 | 50 | 85.6 | 36 | 65.3 | 38 | 223.2 | 216.7 | 216.7 | YES
9 | OK | 17 | 16 | 16 | 66 | 44.9 | 6.76 | 50 | 85.6 | 36 | 69.7 | 37.6 | 222.4 | 218.1 | 218.1 | YES
10 | OK | 54 | 0 | 0 | 66 | 95.4 | 6.74 | 50 | 85.6 | 36 | 69.7 | 38 | 222.2 | 216.7 | 216.7 | YES
11 | OK | 16 | 44 | 44 | 66 | 48 | 3.05 | 50 | 85.6 | 36 | 75.6 | 36 | 220 | 221.5 | 220 | YES
12 | OK | 16 | 45 | 45 | 66 | 47.9 | 3.71 | 50 | 85.6 | 36 | 76.9 | 37.6 | 218.7 | 218.1 | 218.1 | YES
13 | OK | 0 | 1 | 70 | 66 | 112.3 | 5.09 | 50 | 85.6 | 36 | 73.6 | 37.3 | 221.4 | 218.8 | 218.8 | YES
14 | ** OPTIMAL ** | 44 | 5 | 5 | 66 | 50.9 | 3.05 | 50 | 85.6 | 36 | 78.4 | 36 | 220.2 | 221.5 | 220.2 | YES
15 | OK | 5 | 4 | 4 | 66 | 89.4 | 3.05 | 50 | 85.6 | 36 | 78.4 | 38.4 | 220.2 | 215.6 | 215.6 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 45-031780
TR_B (available) | 22-005677
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 85.6
TR_B Baseline Loading% | 36
Total Scenarios Evaluated | 22
Feasible Scenarios | 15
--- Optimal Solution ---
Switch Parent Node | 44
Switch Child Node | 5
Tie Node (TR_A side) | 5
Tie Node (TR_B side) | 66
Tie Line Distance (m) | 50.9
Load Transferred (kW) | 3.05
TR_A Loading After (%) | 78.4
TR_B Loading After (%) | 36
Minimum Voltage (V) | 220.2