## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 27 | 28 | 35 | 43 | 59.8 | 4.99 | 50 | 85.6 | 73.3 | 74.1 | 76.6 | 220.6 | 216.1 | 216.1 | YES
2 | OK | 28 | 29 | 35 | 43 | 59.8 | 4.35 | 50 | 85.6 | 73.3 | 75.2 | 76.4 | 220.6 | 216.1 | 216.1 | YES
3 | OK | 29 | 36 | 37 | 33 | 84.3 | 3.3 | 50 | 85.6 | 73.3 | 78 | 75.1 | 220 | 215.8 | 215.8 | YES
4 | OK | 16 | 44 | 44 | 62 | 148.7 | 3.05 | 50 | 85.6 | 73.3 | 75.6 | 73.3 | 220 | 216.1 | 216.1 | YES
5 | ** OPTIMAL ** | 16 | 45 | 47 | 62 | 108.4 | 3.71 | 50 | 85.6 | 73.3 | 76.9 | 73.7 | 218.7 | 216.1 | 216.1 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 45-031780
TR_B (available) | 29-005428
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 85.6
TR_B Baseline Loading% | 73.3
Total Scenarios Evaluated | 5
Feasible Scenarios | 5
--- Optimal Solution ---
Switch Parent Node | 16
Switch Child Node | 45
Tie Node (TR_A side) | 47
Tie Node (TR_B side) | 62
Tie Line Distance (m) | 108.4
Load Transferred (kW) | 3.71
TR_A Loading After (%) | 76.9
TR_B Loading After (%) | 73.7
Minimum Voltage (V) | 216.1