## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 43 | 53 | 19 | 7 | 39.6 | 9.96 | 50 | 85.6 | 23 | 62.2 | 34.4 | 223 | 218 | 218 | YES
| NG | 43 | 17 | 52 | 7 | 63.2 | 7.54 | 50 | 85.6 | 23 | 67.9 | 54 | 222.3 | 204.7 | 204.7 | NO
2 | ** OPTIMAL ** | 53 | 54 | 19 | 7 | 39.6 | 8.64 | 50 | 85.6 | 23 | 65.3 | 29.1 | 223.2 | 219.8 | 219.8 | YES
| NG | 17 | 16 | 52 | 7 | 63.2 | 6.76 | 50 | 85.6 | 23 | 69.7 | 50.5 | 222.4 | 207.2 | 207.2 | NO
3 | OK | 54 | 0 | 19 | 7 | 39.6 | 6.74 | 50 | 85.6 | 23 | 69.7 | 29.1 | 222.2 | 219.8 | 219.8 | YES
4 | OK | 16 | 44 | 52 | 7 | 63.2 | 3.05 | 50 | 85.6 | 23 | 75.6 | 35 | 220 | 218.6 | 218.6 | YES
5 | OK | 0 | 1 | 19 | 7 | 39.6 | 5.09 | 50 | 85.6 | 23 | 73.6 | 29.1 | 221.4 | 219.8 | 219.8 | YES
6 | OK | 44 | 5 | 52 | 7 | 63.2 | 3.05 | 50 | 85.6 | 23 | 78.4 | 35 | 220.2 | 218.6 | 218.6 | YES
7 | OK | 5 | 4 | 52 | 7 | 63.2 | 3.05 | 50 | 85.6 | 23 | 78.4 | 35 | 220.2 | 218.6 | 218.6 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 45-031780
TR_B (available) | 42-006080
TR_A Rated kVA | 50
TR_B Rated kVA | 30
TR_A Baseline Loading% | 85.6
TR_B Baseline Loading% | 23
Total Scenarios Evaluated | 9
Feasible Scenarios | 7
--- Optimal Solution ---
Switch Parent Node | 53
Switch Child Node | 54
Tie Node (TR_A side) | 19
Tie Node (TR_B side) | 7
Tie Line Distance (m) | 39.6
Load Transferred (kW) | 8.64
TR_A Loading After (%) | 65.3
TR_B Loading After (%) | 29.1
Minimum Voltage (V) | 219.8