## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 14 | 15 | 65 | 2 | 204.2 | 21.54 | 50 | 85.6 | 6.1 | 35.4 | 34.4 | 226.5 | 212.9 | 212.9 | YES
2 | OK | 15 | 41 | 65 | 2 | 204.2 | 20.89 | 50 | 85.6 | 6.1 | 36.9 | 34.4 | 226.2 | 212.9 | 212.9 | YES
3 | OK | 41 | 42 | 65 | 2 | 204.2 | 18.27 | 50 | 85.6 | 6.1 | 42.9 | 23.5 | 226.2 | 220 | 220 | YES
4 | OK | 42 | 43 | 65 | 2 | 204.2 | 17.5 | 50 | 85.6 | 6.1 | 44.7 | 23.5 | 225.8 | 220 | 220 | YES
5 | OK | 43 | 53 | 65 | 2 | 204.2 | 9.96 | 50 | 85.6 | 6.1 | 62.2 | 17.2 | 223 | 224.2 | 223 | YES
6 | ** OPTIMAL ** | 53 | 54 | 65 | 2 | 204.2 | 8.64 | 50 | 85.6 | 6.1 | 65.3 | 12.1 | 223.2 | 227.1 | 223.2 | YES
7 | OK | 54 | 0 | 65 | 2 | 204.2 | 6.74 | 50 | 85.6 | 6.1 | 69.7 | 12.1 | 222.2 | 227.1 | 222.2 | YES
8 | OK | 0 | 1 | 65 | 2 | 204.2 | 5.09 | 50 | 85.6 | 6.1 | 73.6 | 12.1 | 221.4 | 227.1 | 221.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 45-031780
TR_B (available) | 64-014225
TR_A Rated kVA | 50
TR_B Rated kVA | 30
TR_A Baseline Loading% | 85.6
TR_B Baseline Loading% | 6.1
Total Scenarios Evaluated | 8
Feasible Scenarios | 8
--- Optimal Solution ---
Switch Parent Node | 53
Switch Child Node | 54
Tie Node (TR_A side) | 65
Tie Node (TR_B side) | 2
Tie Line Distance (m) | 204.2
Load Transferred (kW) | 8.64
TR_A Loading After (%) | 65.3
TR_B Loading After (%) | 12.1
Minimum Voltage (V) | 223.2