## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 43 | 53 | 8 | 35 | 52.5 | 9.96 | 50 | 85.6 | 50.8 | 62.2 | 74.2 | 223 | 217.9 | 217.9 | YES
2 | ** OPTIMAL ** | 43 | 17 | 17 | 11 | 145.2 | 7.54 | 50 | 85.6 | 50.8 | 67.9 | 57.6 | 222.3 | 222.2 | 222.2 | YES
3 | OK | 53 | 54 | 8 | 35 | 52.5 | 8.64 | 50 | 85.6 | 50.8 | 65.3 | 71.1 | 223.2 | 217.8 | 217.8 | YES
4 | OK | 54 | 0 | 8 | 35 | 52.5 | 6.74 | 50 | 85.6 | 50.8 | 69.7 | 66.5 | 222.2 | 222.3 | 222.2 | YES
5 | OK | 0 | 1 | 8 | 35 | 52.5 | 5.09 | 50 | 85.6 | 50.8 | 73.6 | 62.6 | 221.4 | 223.1 | 221.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 45-031780
TR_B (available) | 67-012639
TR_A Rated kVA | 50
TR_B Rated kVA | 50
TR_A Baseline Loading% | 85.6
TR_B Baseline Loading% | 50.8
Total Scenarios Evaluated | 5
Feasible Scenarios | 5
--- Optimal Solution ---
Switch Parent Node | 43
Switch Child Node | 17
Tie Node (TR_A side) | 17
Tie Node (TR_B side) | 11
Tie Line Distance (m) | 145.2
Load Transferred (kW) | 7.54
TR_A Loading After (%) | 67.9
TR_B Loading After (%) | 57.6
Minimum Voltage (V) | 222.2