## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 7 | 6 | 8 | 47 | 1 | 14.71 | 50 | 86 | 36.5 | 52.3 | 47.6 | 221.5 | 213.2 | 213.2 | YES
2 | OK | 7 | 21 | 39 | 92 | 11.6 | 21.64 | 50 | 86 | 36.5 | 33.7 | 53.2 | 225.9 | 211.2 | 211.2 | YES
3 | OK | 6 | 24 | 8 | 47 | 1 | 5.42 | 50 | 86 | 36.5 | 73.6 | 40.4 | 217.9 | 219 | 217.9 | YES
4 | OK | 21 | 22 | 39 | 92 | 11.6 | 16.05 | 50 | 86 | 36.5 | 48.8 | 48.8 | 225.4 | 212.4 | 212.4 | YES
5 | OK | 21 | 0 | 5 | 30 | 37.9 | 3.2 | 50 | 86 | 36.5 | 78.7 | 38.9 | 217.5 | 217.4 | 217.4 | YES
6 | OK | 24 | 23 | 8 | 47 | 1 | 4.65 | 50 | 86 | 36.5 | 75.3 | 39.9 | 217.8 | 219.1 | 217.8 | YES
7 | OK | 22 | 25 | 39 | 92 | 11.6 | 16.05 | 50 | 86 | 36.5 | 48.8 | 48.8 | 225.4 | 212.4 | 212.4 | YES
8 | OK | 25 | 12 | 39 | 92 | 11.6 | 15.54 | 50 | 86 | 36.5 | 50 | 48.4 | 225.4 | 212.3 | 212.3 | YES
9 | ** OPTIMAL ** | 12 | 13 | 44 | 69 | 15.9 | 4.31 | 50 | 86 | 36.5 | 76 | 39.7 | 218.7 | 219.3 | 218.7 | YES
10 | OK | 12 | 14 | 39 | 92 | 11.6 | 11.23 | 50 | 86 | 36.5 | 59.9 | 45 | 223.9 | 215.4 | 215.4 | YES
11 | OK | 14 | 15 | 39 | 92 | 11.6 | 10.24 | 50 | 86 | 36.5 | 62.2 | 44.2 | 224 | 215.3 | 215.3 | YES
12 | OK | 15 | 16 | 39 | 92 | 11.6 | 8.56 | 50 | 86 | 36.5 | 65.6 | 43 | 224.1 | 214.7 | 214.7 | YES
13 | OK | 16 | 29 | 39 | 92 | 11.6 | 7.67 | 50 | 86 | 36.5 | 68.1 | 42.3 | 224.1 | 214.4 | 214.4 | YES
14 | OK | 29 | 30 | 39 | 92 | 11.6 | 6.62 | 50 | 86 | 36.5 | 70.5 | 41.5 | 223.7 | 214.2 | 214.2 | YES
15 | OK | 30 | 17 | 39 | 92 | 11.6 | 6.44 | 50 | 86 | 36.5 | 71 | 41.4 | 223.5 | 214.1 | 214.1 | YES
16 | OK | 17 | 19 | 39 | 92 | 11.6 | 4.9 | 50 | 86 | 36.5 | 74.5 | 40.3 | 223.7 | 214 | 214 | YES
17 | OK | 19 | 39 | 39 | 92 | 11.6 | 4.9 | 50 | 86 | 36.5 | 74.5 | 40 | 223.7 | 213.8 | 213.8 | YES
18 | OK | 39 | 40 | 40 | 92 | 22.9 | 4.45 | 50 | 86 | 36.5 | 75.6 | 39.9 | 223.2 | 214 | 214 | YES
19 | OK | 40 | 50 | 50 | 85 | 55.9 | 4.36 | 50 | 86 | 36.5 | 75.8 | 39.8 | 223.2 | 218 | 218 | YES
20 | OK | 50 | 45 | 45 | 85 | 69.9 | 4.29 | 50 | 86 | 36.5 | 75.9 | 39.7 | 223.2 | 218.2 | 218.2 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 45-031794
TR_B (available) | 59-001010
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 86
TR_B Baseline Loading% | 36.5
Total Scenarios Evaluated | 20
Feasible Scenarios | 20
--- Optimal Solution ---
Switch Parent Node | 12
Switch Child Node | 13
Tie Node (TR_A side) | 44
Tie Node (TR_B side) | 69
Tie Line Distance (m) | 15.9
Load Transferred (kW) | 4.31
TR_A Loading After (%) | 76
TR_B Loading After (%) | 39.7
Minimum Voltage (V) | 218.7