## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 8 | 17 | 89 | 25 | 84.6 | 5.03 | 50 | 75 | 47.8 | 63 | 55.1 | 219 | 210.2 | 210.2 | YES
2 | OK | 8 | 29 | 63 | 25 | 37 | 5.18 | 50 | 75 | 47.8 | 62.8 | 53.8 | 216.2 | 210.6 | 210.6 | YES
3 | OK | 17 | 100 | 89 | 25 | 84.6 | 3.7 | 50 | 75 | 47.8 | 66.1 | 55.1 | 218.5 | 210.2 | 210.2 | YES
4 | OK | 29 | 30 | 63 | 25 | 37 | 4.29 | 50 | 75 | 47.8 | 64.8 | 53.8 | 216.3 | 210.6 | 210.6 | YES
5 | OK | 100 | 93 | 89 | 25 | 84.6 | 3.28 | 50 | 75 | 47.8 | 67.1 | 53.4 | 218.5 | 210.7 | 210.7 | YES
6 | OK | 30 | 39 | 63 | 25 | 37 | 4.1 | 50 | 75 | 47.8 | 65.2 | 53 | 216.3 | 210.8 | 210.8 | YES
7 | OK | 93 | 92 | 89 | 25 | 84.6 | 3.02 | 50 | 75 | 47.8 | 67.7 | 52.3 | 218.4 | 211 | 211 | YES
8 | OK | 39 | 94 | 63 | 25 | 37 | 3.6 | 50 | 75 | 47.8 | 66.4 | 53 | 215.7 | 210.8 | 210.8 | YES
9 | OK | 92 | 89 | 89 | 25 | 84.6 | 2.9 | 50 | 75 | 47.8 | 68 | 51.8 | 218.3 | 211.2 | 211.2 | YES
10 | OK | 94 | 58 | 63 | 25 | 37 | 3.39 | 50 | 75 | 47.8 | 66.9 | 53 | 215.5 | 210.8 | 210.8 | YES
11 | OK | 89 | 16 | 16 | 25 | 85.3 | 2.9 | 50 | 75 | 47.8 | 68 | 51.8 | 218.3 | 211.2 | 211.2 | YES
12 | OK | 58 | 59 | 63 | 25 | 37 | 2.77 | 50 | 75 | 47.8 | 68.4 | 53 | 215.1 | 210.8 | 210.8 | YES
13 | OK | 16 | 3 | 3 | 25 | 95.9 | 2.47 | 50 | 75 | 47.8 | 69 | 51 | 218.1 | 211.4 | 211.4 | YES
14 | OK | 59 | 60 | 63 | 25 | 37 | 1.83 | 50 | 75 | 47.8 | 70.6 | 50.6 | 214.8 | 211.5 | 211.5 | YES
15 | OK | 3 | 2 | 2 | 25 | 97.4 | 2.47 | 50 | 75 | 47.8 | 69 | 51 | 218.1 | 211.4 | 211.4 | YES
16 | OK | 60 | 61 | 63 | 25 | 37 | 1.75 | 50 | 75 | 47.8 | 70.8 | 50.6 | 214.7 | 211.5 | 211.5 | YES
17 | OK | 2 | 76 | 75 | 25 | 101.6 | 1.72 | 50 | 75 | 47.8 | 70.8 | 48 | 217.3 | 212.3 | 212.3 | YES
18 | OK | 61 | 90 | 63 | 25 | 37 | 1.17 | 50 | 75 | 47.8 | 72.2 | 48.3 | 214.7 | 212.2 | 212.2 | YES
19 | OK | 76 | 74 | 75 | 25 | 101.6 | 1.72 | 50 | 75 | 47.8 | 70.8 | 48 | 217.3 | 212.3 | 212.3 | YES
20 | ** OPTIMAL ** | 90 | 63 | 63 | 25 | 37 | 1.04 | 50 | 75 | 47.8 | 72.5 | 47.8 | 214.7 | 212.3 | 212.3 | YES
21 | OK | 74 | 75 | 75 | 25 | 101.6 | 0.06 | 50 | 75 | 47.8 | 74.8 | 48 | 214.2 | 212.3 | 212.3 | YES
22 | OK | 74 | 15 | 15 | 25 | 120.6 | 1.66 | 50 | 75 | 47.8 | 70.9 | 54.5 | 217.2 | 210.4 | 210.4 | YES
23 | OK | 63 | 32 | 32 | 25 | 37.3 | 0.6 | 50 | 75 | 47.8 | 73.6 | 47.8 | 214.2 | 212.3 | 212.3 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 46-001336
TR_B (available) | 57-012585
TR_A Rated kVA | 50
TR_B Rated kVA | 30
TR_A Baseline Loading% | 75
TR_B Baseline Loading% | 47.8
Total Scenarios Evaluated | 23
Feasible Scenarios | 23
--- Optimal Solution ---
Switch Parent Node | 90
Switch Child Node | 63
Tie Node (TR_A side) | 63
Tie Node (TR_B side) | 25
Tie Line Distance (m) | 37
Load Transferred (kW) | 1.04
TR_A Loading After (%) | 72.5
TR_B Loading After (%) | 47.8
Minimum Voltage (V) | 212.3