## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 65 | 66 | 9 | 28 | 163.6 | 15.61 | 50 | 75 | 20.5 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 66 | 67 | 9 | 28 | 163.6 | 15.61 | 50 | 75 | 20.5 | 38.5 | 40.2 | 216.6 | 198.3 | 198.3 | NO
1 | OK | 67 | 72 | 9 | 28 | 163.6 | 3.48 | 50 | 75 | 20.5 | 66.8 | 24.6 | 215.8 | 217.8 | 215.8 | YES
2 | OK | 72 | 73 | 9 | 28 | 163.6 | 3.48 | 50 | 75 | 20.5 | 66.8 | 24.6 | 215.8 | 217.8 | 215.8 | YES
3 | OK | 73 | 81 | 9 | 28 | 163.6 | 3.04 | 50 | 75 | 20.5 | 67.8 | 24 | 215.8 | 218.2 | 215.8 | YES
4 | OK | 81 | 4 | 11 | 28 | 175.4 | 0.92 | 50 | 75 | 20.5 | 72.8 | 21.5 | 214.8 | 218.2 | 214.8 | YES
5 | OK | 81 | 82 | 9 | 28 | 163.6 | 2.12 | 50 | 75 | 20.5 | 67.8 | 22.9 | 215.8 | 218 | 215.8 | YES
6 | OK | 4 | 5 | 11 | 28 | 175.4 | 0.09 | 50 | 75 | 20.5 | 72.8 | 20.6 | 214.8 | 218 | 214.8 | YES
7 | OK | 82 | 6 | 9 | 28 | 163.6 | 1.83 | 50 | 75 | 20.5 | 68.5 | 22.6 | 215.8 | 218.3 | 215.8 | YES
8 | OK | 5 | 11 | 11 | 28 | 175.4 | 0.09 | 50 | 75 | 20.5 | 72.8 | 20.6 | 214.8 | 218 | 214.8 | YES
9 | ** OPTIMAL ** | 6 | 10 | 10 | 28 | 175.3 | 1.83 | 50 | 75 | 20.5 | 68.5 | 22.6 | 215.8 | 218.3 | 215.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 46-001336
TR_B (available) | 66-017978
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 75
TR_B Baseline Loading% | 20.5
Total Scenarios Evaluated | 11
Feasible Scenarios | 9
--- Optimal Solution ---
Switch Parent Node | 6
Switch Child Node | 10
Tie Node (TR_A side) | 10
Tie Node (TR_B side) | 28
Tie Line Distance (m) | 175.3
Load Transferred (kW) | 1.83
TR_A Loading After (%) | 68.5
TR_B Loading After (%) | 22.6
Minimum Voltage (V) | 215.8