## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 11 | 12 | 0 | 11 | 33.8 | 26.07 | 50 | 61.3 | 28.7 | [5 empty] | NO | TR_A sim: ไม่พบสาย backbone: TAG มี 'LC'
| NG | 12 | 13 | 0 | 11 | 33.8 | 22.67 | 50 | 61.3 | 28.7 | 7.8 | 45.9 | 229.5 | 207.8 | 207.8 | NO
| NG | 13 | 3 | 0 | 11 | 33.8 | 21.77 | 50 | 61.3 | 28.7 | 9.9 | 45.1 | 228.7 | 209.4 | 209.4 | NO
1 | OK | 3 | 2 | 0 | 11 | 33.8 | 16.64 | 50 | 61.3 | 28.7 | 21.7 | 41.2 | 225.9 | 213.2 | 213.2 | YES
2 | OK | 3 | 4 | 1 | 11 | 40.6 | 5.13 | 50 | 61.3 | 28.7 | 49.1 | 32.4 | 214.5 | 225.3 | 214.5 | YES
3 | OK | 2 | 10 | 0 | 11 | 33.8 | 16 | 50 | 61.3 | 28.7 | 23.2 | 40.6 | 225.3 | 214.1 | 214.1 | YES
4 | OK | 4 | 5 | 1 | 11 | 40.6 | 4.27 | 50 | 61.3 | 28.7 | 51.1 | 31.8 | 214.6 | 226.1 | 214.6 | YES
5 | OK | 10 | 9 | 0 | 11 | 33.8 | 7.71 | 50 | 61.3 | 28.7 | 42.9 | 34.3 | 217.4 | 224.1 | 217.4 | YES
6 | OK | 5 | 6 | 1 | 11 | 40.6 | 3.12 | 50 | 61.3 | 28.7 | 53.8 | 30.9 | 214.3 | 226.4 | 214.3 | YES
7 | ** OPTIMAL ** | 9 | 8 | 0 | 11 | 33.8 | 7.71 | 50 | 61.3 | 28.7 | 42.9 | 34.3 | 217.4 | 224.1 | 217.4 | YES
8 | OK | 6 | 1 | 1 | 11 | 40.6 | 1.92 | 50 | 61.3 | 28.7 | 56.6 | 30.1 | 213.9 | 226.5 | 213.9 | YES
9 | OK | 8 | 7 | 0 | 11 | 33.8 | 3.98 | 50 | 61.3 | 28.7 | 51.9 | 31.5 | 214.1 | 226.5 | 214.1 | YES
10 | OK | 7 | 0 | 0 | 11 | 33.8 | 1.22 | 50 | 61.3 | 28.7 | 58.5 | 29.6 | 212 | 226.7 | 212 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 46-005683
TR_B (available) | 28-001118
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 61.3
TR_B Baseline Loading% | 28.7
Total Scenarios Evaluated | 13
Feasible Scenarios | 10
--- Optimal Solution ---
Switch Parent Node | 9
Switch Child Node | 8
Tie Node (TR_A side) | 0
Tie Node (TR_B side) | 11
Tie Line Distance (m) | 33.8
Load Transferred (kW) | 7.71
TR_A Loading After (%) | 42.9
TR_B Loading After (%) | 34.3
Minimum Voltage (V) | 217.4