## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 11 | 12 | 15 | 33 | 17.4 | 26.07 | 50 | 61.3 | 33.3 | [5 empty] | NO | TR_A sim: ไม่พบสาย backbone: TAG มี 'LC'
| NG | 12 | 13 | 18 | 33 | 37.7 | 22.67 | 50 | 61.3 | 33.3 | 7.8 | 45 | 229.5 | 198.3 | 198.3 | NO
1 | OK | 12 | 14 | 15 | 33 | 17.4 | 3.4 | 50 | 61.3 | 33.3 | 53.1 | 34.9 | 214.8 | 221.1 | 214.8 | YES
| NG | 13 | 3 | 18 | 33 | 37.7 | 21.77 | 50 | 61.3 | 33.3 | 9.9 | 44.5 | 228.7 | 199.9 | 199.9 | NO
2 | OK | 14 | 15 | 15 | 33 | 17.4 | 2.4 | 50 | 61.3 | 33.3 | 55.7 | 34.4 | 213.1 | 222.2 | 213.1 | YES
| NG | 3 | 2 | 18 | 33 | 37.7 | 16.64 | 50 | 61.3 | 33.3 | 21.7 | 41.8 | 225.9 | 203.1 | 203.1 | NO
3 | OK | 3 | 4 | 4 | 33 | 57.2 | 5.13 | 50 | 61.3 | 33.3 | 49.1 | 35.7 | 214.5 | 220 | 214.5 | YES
| NG | 2 | 17 | 18 | 33 | 37.7 | 0.64 | 50 | 61.3 | 33.3 | 193.2 | 33.6 | 20 | 222.2 | 20 | NO
| NG | 2 | 10 | 10 | 34 | 67.2 | 16 | 50 | 61.3 | 33.3 | 23.2 | 41.3 | 225.3 | 209.1 | 209.1 | NO
4 | OK | 4 | 5 | 5 | 33 | 72.7 | 4.27 | 50 | 61.3 | 33.3 | 51.1 | 35.3 | 214.6 | 219.6 | 214.6 | YES
5 | OK | 10 | 9 | 19 | 34 | 67.7 | 7.71 | 50 | 61.3 | 33.3 | 42.9 | 37 | 217.4 | 218.8 | 217.4 | YES
6 | OK | 5 | 6 | 6 | 34 | 124.8 | 3.12 | 50 | 61.3 | 33.3 | 53.8 | 34.8 | 214.3 | 221.2 | 214.3 | YES
7 | ** OPTIMAL ** | 9 | 8 | 8 | 34 | 96.4 | 7.71 | 50 | 61.3 | 33.3 | 42.9 | 37 | 217.4 | 218.9 | 217.4 | YES
8 | OK | 8 | 7 | 7 | 34 | 123.7 | 3.98 | 50 | 61.3 | 33.3 | 51.9 | 35.2 | 214.1 | 221.5 | 214.1 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 46-005683
TR_B (available) | 66-016684
TR_A Rated kVA | 50
TR_B Rated kVA | 250
TR_A Baseline Loading% | 61.3
TR_B Baseline Loading% | 33.3
Total Scenarios Evaluated | 14
Feasible Scenarios | 8
--- Optimal Solution ---
Switch Parent Node | 9
Switch Child Node | 8
Tie Node (TR_A side) | 8
Tie Node (TR_B side) | 34
Tie Line Distance (m) | 96.4
Load Transferred (kW) | 7.71
TR_A Loading After (%) | 42.9
TR_B Loading After (%) | 37
Minimum Voltage (V) | 217.4