## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 3 | 82 | 73 | 5 | 2.7 | 18.9 | 50 | 23.8 | 9.6 | 8.9 | 34.9 | 225.7 | 208.8 | 208.8 | NO
| NG | 82 | 134 | 73 | 5 | 2.7 | 17.6 | 50 | 23.8 | 9.6 | 8.9 | 34.9 | 225.7 | 208.8 | 208.8 | NO
| NG | 134 | 135 | 73 | 5 | 2.7 | 17.21 | 50 | 23.8 | 9.6 | 8.9 | 34.9 | 225.7 | 208.8 | 208.8 | NO
| NG | 135 | 136 | 73 | 5 | 2.7 | 17.21 | 50 | 23.8 | 9.6 | 8.9 | 34.9 | 225.7 | 208.8 | 208.8 | NO
1 | OK | 136 | 45 | 73 | 5 | 2.7 | 8.2 | 50 | 23.8 | 9.6 | 14.4 | 25 | 221.1 | 218 | 218 | YES
2 | OK | 45 | 44 | 73 | 5 | 2.7 | 8.08 | 50 | 23.8 | 9.6 | 14.4 | 25 | 221.1 | 218 | 218 | YES
3 | OK | 44 | 138 | 73 | 5 | 2.7 | 4.87 | 50 | 23.8 | 9.6 | 18.9 | 17.4 | 218.6 | 224.9 | 218.6 | YES
4 | ** OPTIMAL ** | 138 | 137 | 73 | 5 | 2.7 | 4.87 | 50 | 23.8 | 9.6 | 18.9 | 17.4 | 218.6 | 224.9 | 218.6 | YES
5 | OK | 137 | 63 | 73 | 5 | 2.7 | 4.45 | 50 | 23.8 | 9.6 | 19.8 | 15.8 | 218.1 | 225.9 | 218.1 | YES
6 | OK | 63 | 64 | 73 | 5 | 2.7 | 4.39 | 50 | 23.8 | 9.6 | 20 | 15.6 | 218 | 226.1 | 218 | YES
7 | OK | 64 | 66 | 73 | 5 | 2.7 | 4.24 | 50 | 23.8 | 9.6 | 20 | 15.6 | 218 | 226.1 | 218 | YES
8 | OK | 66 | 65 | 73 | 5 | 2.7 | 1.56 | 50 | 23.8 | 9.6 | 20 | 15.6 | 218 | 226.1 | 218 | YES
9 | OK | 65 | 67 | 73 | 5 | 2.7 | 1.56 | 50 | 23.8 | 9.6 | 20 | 15.6 | 218 | 226.1 | 218 | YES
10 | OK | 67 | 123 | 73 | 5 | 2.7 | 1.01 | 50 | 23.8 | 9.6 | 21.3 | 13.4 | 217.3 | 227.1 | 217.3 | YES
11 | OK | 123 | 122 | 73 | 5 | 2.7 | 1.01 | 50 | 23.8 | 9.6 | 21.3 | 13.4 | 217.3 | 227.1 | 217.3 | YES
12 | OK | 122 | 74 | 73 | 5 | 2.7 | 0.33 | 50 | 23.8 | 9.6 | 23 | 10.8 | 216.4 | 227.6 | 216.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 46-005706
TR_B (available) | 65-003881
TR_A Rated kVA | 50
TR_B Rated kVA | 30
TR_A Baseline Loading% | 23.8
TR_B Baseline Loading% | 9.6
Total Scenarios Evaluated | 16
Feasible Scenarios | 12
--- Optimal Solution ---
Switch Parent Node | 138
Switch Child Node | 137
Tie Node (TR_A side) | 73
Tie Node (TR_B side) | 5
Tie Line Distance (m) | 2.7
Load Transferred (kW) | 4.87
TR_A Loading After (%) | 18.9
TR_B Loading After (%) | 17.4
Minimum Voltage (V) | 218.6