## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 18 | 19 | 22 | 4 | 3.1 | 17.79 | 50 | 109.1 | 19.4 | 39 | 88.5 | 223.4 | 214.1 | 214.1 | NO
| NG | 19 | 20 | 22 | 4 | 3.1 | 16.29 | 50 | 109.1 | 19.4 | 44.8 | 82.6 | 222.3 | 215.8 | 215.8 | NO
1 | OK | 20 | 22 | 22 | 4 | 3.1 | 14.31 | 50 | 109.1 | 19.4 | 52.4 | 75 | 222.3 | 215.7 | 215.7 | YES
2 | ** OPTIMAL ** | 22 | 21 | 21 | 4 | 37.5 | 10.12 | 50 | 109.1 | 19.4 | 68.7 | 58.8 | 221.5 | 217 | 217 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 47-000662
TR_B (available) | 65-023796
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 109.1
TR_B Baseline Loading% | 19.4
Total Scenarios Evaluated | 4
Feasible Scenarios | 2
--- Optimal Solution ---
Switch Parent Node | 22
Switch Child Node | 21
Tie Node (TR_A side) | 21
Tie Node (TR_B side) | 4
Tie Line Distance (m) | 37.5
Load Transferred (kW) | 10.12
TR_A Loading After (%) | 68.7
TR_B Loading After (%) | 58.8
Minimum Voltage (V) | 217