## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 2 | 3 | 3 | 6 | 106 | 14.86 | 50 | 87.9 | 24 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 2 | 34 | 10 | 3 | 41.5 | 7.77 | 50 | 87.9 | 24 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 3 | 16 | 16 | 6 | 107 | 14.86 | 50 | 87.9 | 24 | 30.1 | 84.1 | 220.4 | 202 | 202 | NO
| NG | 34 | 33 | 10 | 3 | 41.5 | 7.77 | 50 | 87.9 | 24 | 57.7 | 55.2 | 215.2 | 208 | 208 | NO
| NG | 16 | 17 | 17 | 6 | 109.3 | 14.86 | 50 | 87.9 | 24 | 30.1 | 83.6 | 220.4 | 202.3 | 202.3 | NO
| NG | 33 | 53 | 10 | 3 | 41.5 | 7.77 | 50 | 87.9 | 24 | 57.7 | 55.2 | 215.2 | 208 | 208 | NO
1 | OK | 17 | 45 | 45 | 6 | 125.4 | 4.33 | 50 | 87.9 | 24 | 71 | 40.9 | 212.1 | 218.1 | 212.1 | YES
| NG | 17 | 18 | 18 | 6 | 119.2 | 10.28 | 50 | 87.9 | 24 | 47.7 | 64.9 | 216.9 | 209.4 | 209.4 | NO
2 | OK | 53 | 32 | 30 | 2 | 75.4 | 5.81 | 50 | 87.9 | 24 | 65.2 | 46.9 | 213.6 | 214.8 | 213.6 | YES
3 | OK | 45 | 46 | 46 | 6 | 130.8 | 4.29 | 50 | 87.9 | 24 | 71.1 | 40.7 | 212.1 | 218.2 | 212.1 | YES
4 | OK | 18 | 19 | 19 | 7 | 130.8 | 9.75 | 50 | 87.9 | 24 | 49.8 | 62.2 | 216.5 | 212.8 | 212.8 | YES
5 | OK | 32 | 31 | 30 | 2 | 75.4 | 5.81 | 50 | 87.9 | 24 | 65.2 | 46.9 | 213.6 | 214.8 | 213.6 | YES
6 | OK | 46 | 47 | 47 | 6 | 135.4 | 4.07 | 50 | 87.9 | 24 | 72 | 39.9 | 211.9 | 218.5 | 211.9 | YES
7 | ** OPTIMAL ** | 19 | 7 | 7 | 7 | 134.1 | 9.75 | 50 | 87.9 | 24 | 49.8 | 57 | 216.5 | 214.6 | 214.6 | YES
8 | OK | 31 | 30 | 30 | 2 | 75.4 | 5.81 | 50 | 87.9 | 24 | 65.2 | 46.9 | 213.6 | 214.8 | 213.6 | YES
9 | OK | 47 | 48 | 48 | 6 | 140.7 | 4.07 | 50 | 87.9 | 24 | 72 | 39.9 | 211.9 | 218.5 | 211.9 | YES
10 | OK | 30 | 29 | 29 | 2 | 87.8 | 5.81 | 50 | 87.9 | 24 | 65.2 | 46.8 | 213.6 | 215.4 | 213.6 | YES
11 | OK | 48 | 49 | 49 | 6 | 144.6 | 4.07 | 50 | 87.9 | 24 | 72 | 39.9 | 211.9 | 218.5 | 211.9 | YES
12 | OK | 29 | 1 | 1 | 2 | 91 | 4.84 | 50 | 87.9 | 24 | 68.9 | 43 | 212.8 | 217 | 212.8 | YES
13 | OK | 49 | 50 | 50 | 6 | 148.3 | 3.91 | 50 | 87.9 | 24 | 72.6 | 39.2 | 211.7 | 218.7 | 211.7 | YES
14 | OK | 1 | 0 | 0 | 2 | 118.2 | 3.82 | 50 | 87.9 | 24 | 72.9 | 38.9 | 212 | 218.8 | 212 | YES
15 | OK | 0 | 22 | 21 | 2 | 147.3 | 3.76 | 50 | 87.9 | 24 | 73.1 | 38.7 | 211.9 | 219 | 211.9 | YES
16 | OK | 22 | 23 | 21 | 2 | 147.3 | 2.49 | 50 | 87.9 | 24 | 78 | 33.7 | 210.9 | 220.6 | 210.9 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 47-003191
TR_B (available) | 59-012374
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 87.9
TR_B Baseline Loading% | 24
Total Scenarios Evaluated | 23
Feasible Scenarios | 16
--- Optimal Solution ---
Switch Parent Node | 19
Switch Child Node | 7
Tie Node (TR_A side) | 7
Tie Node (TR_B side) | 7
Tie Line Distance (m) | 134.1
Load Transferred (kW) | 9.75
TR_A Loading After (%) | 49.8
TR_B Loading After (%) | 57
Minimum Voltage (V) | 214.6