## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 2 | 3 | 58 | 45 | 73.9 | 14.86 | 50 | 87.9 | 48.7 | 30.1 | 70.3 | 220.4 | 175.1 | 175.1 | NO
| NG | 3 | 16 | 58 | 45 | 73.9 | 14.86 | 50 | 87.9 | 48.7 | 30.1 | 70.3 | 220.4 | 175.1 | 175.1 | NO
| NG | 16 | 17 | 58 | 45 | 73.9 | 14.86 | 50 | 87.9 | 48.7 | 30.1 | 70.1 | 220.4 | 175.5 | 175.5 | NO
1 | ** OPTIMAL ** | 17 | 45 | 58 | 45 | 73.9 | 4.33 | 50 | 87.9 | 48.7 | 71 | 54 | 212.1 | 215.6 | 212.1 | YES
2 | OK | 45 | 46 | 58 | 45 | 73.9 | 4.29 | 50 | 87.9 | 48.7 | 71.1 | 53.9 | 212.1 | 215.7 | 212.1 | YES
3 | OK | 46 | 47 | 58 | 45 | 73.9 | 4.07 | 50 | 87.9 | 48.7 | 72 | 53.7 | 211.9 | 216.3 | 211.9 | YES
4 | OK | 47 | 48 | 58 | 45 | 73.9 | 4.07 | 50 | 87.9 | 48.7 | 72 | 53.7 | 211.9 | 216.3 | 211.9 | YES
5 | OK | 48 | 49 | 58 | 45 | 73.9 | 4.07 | 50 | 87.9 | 48.7 | 72 | 53.7 | 211.9 | 216.3 | 211.9 | YES
6 | OK | 49 | 50 | 58 | 45 | 73.9 | 3.91 | 50 | 87.9 | 48.7 | 72.6 | 53.5 | 211.7 | 216.7 | 211.7 | YES
7 | OK | 50 | 51 | 58 | 45 | 73.9 | 3.91 | 50 | 87.9 | 48.7 | 72.6 | 53.5 | 211.7 | 216.7 | 211.7 | YES
8 | OK | 51 | 14 | 58 | 45 | 73.9 | 3.9 | 50 | 87.9 | 48.7 | 72.6 | 53.5 | 211.7 | 216.7 | 211.7 | YES
9 | OK | 14 | 15 | 58 | 45 | 73.9 | 3.84 | 50 | 87.9 | 48.7 | 72.9 | 53.4 | 211.7 | 216.9 | 211.7 | YES
10 | OK | 15 | 52 | 58 | 45 | 73.9 | 3.77 | 50 | 87.9 | 48.7 | 73.1 | 53.3 | 211.6 | 217 | 211.6 | YES
11 | OK | 52 | 54 | 58 | 45 | 73.9 | 3.77 | 50 | 87.9 | 48.7 | 73.1 | 53.3 | 211.6 | 217 | 211.6 | YES
12 | OK | 54 | 55 | 58 | 45 | 73.9 | 3.02 | 50 | 87.9 | 48.7 | 76 | 52.4 | 211 | 218.8 | 211 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 47-003191
TR_B (available) | 62-001679
TR_A Rated kVA | 30
TR_B Rated kVA | 100
TR_A Baseline Loading% | 87.9
TR_B Baseline Loading% | 48.7
Total Scenarios Evaluated | 15
Feasible Scenarios | 12
--- Optimal Solution ---
Switch Parent Node | 17
Switch Child Node | 45
Tie Node (TR_A side) | 58
Tie Node (TR_B side) | 45
Tie Line Distance (m) | 73.9
Load Transferred (kW) | 4.33
TR_A Loading After (%) | 71
TR_B Loading After (%) | 54
Minimum Voltage (V) | 212.1