## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 23 | 24 | 36 | 0 | 2.1 | 2.69 | 50 | 88.7 | 5.7 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 23 | 28 | 31 | 0 | 143.5 | 20.14 | 50 | 88.7 | 5.7 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 28 | 27 | 27 | 0 | 156.9 | 14.37 | 50 | 88.7 | 5.7 | 32.4 | 43.5 | 226.2 | 195.9 | 195.9 | NO
1 | OK | 28 | 30 | 31 | 0 | 143.5 | 5.77 | 50 | 88.7 | 5.7 | 66.6 | 29.1 | 213.6 | 212.1 | 212.1 | YES
| NG | 27 | 20 | 20 | 0 | 191.4 | 14.01 | 50 | 88.7 | 5.7 | 33.7 | 43.5 | 226.2 | 195.9 | 195.9 | NO
2 | OK | 30 | 10 | 31 | 0 | 143.5 | 5.31 | 50 | 88.7 | 5.7 | 68.3 | 27.1 | 213.2 | 213.4 | 213.2 | YES
| NG | 20 | 19 | 43 | 0 | 207.4 | 13.9 | 50 | 88.7 | 5.7 | 34.2 | 72 | 226.1 | 170.6 | 170.6 | NO
3 | OK | 10 | 11 | 31 | 0 | 143.5 | 4.45 | 50 | 88.7 | 5.7 | 71.6 | 23.4 | 213.2 | 216 | 213.2 | YES
| NG | 19 | 18 | 18 | 0 | 226.3 | 11.69 | 50 | 88.7 | 5.7 | 42.6 | 43 | 225 | 196.6 | 196.6 | NO
4 | OK | 11 | 33 | 33 | 0 | 184.9 | 3.46 | 50 | 88.7 | 5.7 | 75.4 | 16.3 | 213.2 | 221.1 | 213.2 | YES
| NG | 18 | 8 | 8 | 0 | 233.9 | 11.69 | 50 | 88.7 | 5.7 | 42.6 | 43 | 225 | 196.3 | 196.3 | NO
5 | ** OPTIMAL ** | 33 | 32 | 32 | 0 | 208.3 | 3.46 | 50 | 88.7 | 5.7 | 75.4 | 16.3 | 213.2 | 221.3 | 213.2 | YES
| NG | 8 | 7 | 7 | 0 | 241.6 | 9.67 | 50 | 88.7 | 5.7 | 50.4 | 38 | 224 | 200.2 | 200.2 | NO
6 | OK | 32 | 34 | 21 | 0 | 226.3 | 2.9 | 50 | 88.7 | 5.7 | 77.5 | 14 | 212.8 | 223 | 212.8 | YES
| NG | 7 | 26 | 26 | 0 | 265.8 | 9.41 | 50 | 88.7 | 5.7 | 51.4 | 36.8 | 224 | 201.1 | 201.1 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 47-004556
TR_B (available) | 62-005247
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 88.7
TR_B Baseline Loading% | 5.7
Total Scenarios Evaluated | 15
Feasible Scenarios | 6
--- Optimal Solution ---
Switch Parent Node | 33
Switch Child Node | 32
Tie Node (TR_A side) | 32
Tie Node (TR_B side) | 0
Tie Line Distance (m) | 208.3
Load Transferred (kW) | 3.46
TR_A Loading After (%) | 75.4
TR_B Loading After (%) | 16.3
Minimum Voltage (V) | 213.2