## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 23 | 28 | 12 | 25 | 38.3 | 20.14 | 50 | 88.7 | 22.2 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 28 | 27 | 12 | 25 | 38.3 | 14.37 | 50 | 88.7 | 22.2 | 32.4 | 46.6 | 226.2 | 156.1 | 156.1 | NO
| NG | 27 | 20 | 12 | 25 | 38.3 | 14.01 | 50 | 88.7 | 22.2 | 33.7 | 45.6 | 226.2 | 158.9 | 158.9 | NO
| NG | 20 | 19 | 12 | 25 | 38.3 | 13.9 | 50 | 88.7 | 22.2 | 34.2 | 45.3 | 226.1 | 159.7 | 159.7 | NO
| NG | 19 | 18 | 12 | 25 | 38.3 | 11.69 | 50 | 88.7 | 22.2 | 42.6 | 40.2 | 225 | 174.1 | 174.1 | NO
| NG | 18 | 8 | 12 | 25 | 38.3 | 11.69 | 50 | 88.7 | 22.2 | 42.6 | 40.2 | 225 | 174.1 | 174.1 | NO
| NG | 8 | 7 | 12 | 25 | 38.3 | 9.67 | 50 | 88.7 | 22.2 | 50.4 | 36.3 | 224 | 185.3 | 185.3 | NO
| NG | 7 | 26 | 12 | 25 | 38.3 | 9.41 | 50 | 88.7 | 22.2 | 51.4 | 35.9 | 224 | 186.6 | 186.6 | NO
| NG | 26 | 15 | 12 | 25 | 38.3 | 7.5 | 50 | 88.7 | 22.2 | 58.7 | 32.7 | 222 | 195 | 195 | NO
| NG | 15 | 14 | 12 | 25 | 38.3 | 7.1 | 50 | 88.7 | 22.2 | 60.3 | 32 | 221.5 | 196.5 | 196.5 | NO
| NG | 14 | 13 | 12 | 25 | 38.3 | 6.74 | 50 | 88.7 | 22.2 | 61.7 | 31.5 | 221.5 | 197.8 | 197.8 | NO
1 | ** OPTIMAL ** | 13 | 12 | 12 | 25 | 38.3 | 6.41 | 50 | 88.7 | 22.2 | 62.9 | 22.2 | 221.5 | 219.4 | 219.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 47-004556
TR_B (available) | 67-017355
TR_A Rated kVA | 30
TR_B Rated kVA | 100
TR_A Baseline Loading% | 88.7
TR_B Baseline Loading% | 22.2
Total Scenarios Evaluated | 12
Feasible Scenarios | 1
--- Optimal Solution ---
Switch Parent Node | 13
Switch Child Node | 12
Tie Node (TR_A side) | 12
Tie Node (TR_B side) | 25
Tie Line Distance (m) | 38.3
Load Transferred (kW) | 6.41
TR_A Loading After (%) | 62.9
TR_B Loading After (%) | 22.2
Minimum Voltage (V) | 219.4