## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 7 | 28 | 33 | 54 | 1.6 | 1.9 | 50 | 82.3 | 70 | 77.8 | 70 | 221.4 | 218.2 | 218.2 | YES
| NG | 7 | 23 | 2 | 9 | 14.9 | 5.7 | 50 | 82.3 | 70 | 0 | 74.3 | 50 | 216.1 | 50 | NO
2 | OK | 8 | 18 | 24 | 42 | 1.5 | 6.19 | 50 | 82.3 | 70 | 66.1 | 74.6 | 222.1 | 217.7 | 217.7 | YES
3 | OK | 23 | 5 | 2 | 9 | 14.9 | 5.7 | 50 | 82.3 | 70 | 69.2 | 74.3 | 221.7 | 216.1 | 216.1 | YES
4 | OK | 9 | 21 | 25 | 28 | 3 | 7.97 | 50 | 82.3 | 70 | 63.1 | 75.9 | 223.2 | 218 | 218 | YES
5 | OK | 9 | 22 | 13 | 54 | 35.9 | 13.92 | 50 | 82.3 | 70 | 48.1 | 73.7 | 224.6 | 218.2 | 218.2 | YES
6 | OK | 18 | 19 | 24 | 42 | 1.5 | 2.84 | 50 | 82.3 | 70 | 73.8 | 72.1 | 222.2 | 218.2 | 218.2 | YES
7 | OK | 5 | 4 | 2 | 9 | 14.9 | 5.21 | 50 | 82.3 | 70 | 70.3 | 73.9 | 221.7 | 216.9 | 216.9 | YES
8 | OK | 21 | 1 | 25 | 28 | 3 | 7.97 | 50 | 82.3 | 70 | 63.1 | 75.9 | 223.2 | 218 | 218 | YES
9 | OK | 22 | 10 | 13 | 54 | 35.9 | 13.92 | 50 | 82.3 | 70 | 48.1 | 73.7 | 224.6 | 218.2 | 218.2 | YES
10 | ** OPTIMAL ** | 4 | 3 | 2 | 9 | 14.9 | 4.11 | 50 | 82.3 | 70 | 72.8 | 73.1 | 221.6 | 218.3 | 218.3 | YES
11 | OK | 1 | 0 | 25 | 28 | 3 | 2.08 | 50 | 82.3 | 70 | 76.8 | 71.5 | 222 | 218 | 218 | YES
12 | OK | 10 | 11 | 13 | 54 | 35.9 | 12.22 | 50 | 82.3 | 70 | 52.1 | 73.7 | 224.7 | 218.2 | 218.2 | YES
13 | OK | 10 | 17 | 17 | 54 | 124.3 | 1.7 | 50 | 82.3 | 70 | 78.3 | 70 | 221.2 | 218.2 | 218.2 | YES
14 | OK | 3 | 2 | 2 | 9 | 14.9 | 1.41 | 50 | 82.3 | 70 | 79 | 71.1 | 221.4 | 218.2 | 218.2 | YES
15 | OK | 11 | 14 | 14 | 54 | 93.1 | 6.58 | 50 | 82.3 | 70 | 67 | 72.4 | 222 | 218.2 | 218.2 | YES
16 | OK | 11 | 15 | 13 | 54 | 35.9 | 5.64 | 50 | 82.3 | 70 | 67.3 | 71.3 | 222.4 | 218.2 | 218.2 | YES
17 | OK | 14 | 16 | 16 | 54 | 103.8 | 2.87 | 50 | 82.3 | 70 | 75.7 | 70 | 221.3 | 218.2 | 218.2 | YES
18 | OK | 15 | 12 | 13 | 54 | 35.9 | 2.54 | 50 | 82.3 | 70 | 74.4 | 71.3 | 222.8 | 218.2 | 218.2 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 47-007512
TR_B (available) | 58-010469
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 82.3
TR_B Baseline Loading% | 70
Total Scenarios Evaluated | 19
Feasible Scenarios | 18
--- Optimal Solution ---
Switch Parent Node | 4
Switch Child Node | 3
Tie Node (TR_A side) | 2
Tie Node (TR_B side) | 9
Tie Line Distance (m) | 14.9
Load Transferred (kW) | 4.11
TR_A Loading After (%) | 72.8
TR_B Loading After (%) | 73.1
Minimum Voltage (V) | 218.3