## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 2 | 24 | 16 | 10 | 2.3 | 13.99 | 50 | 87.4 | 30.4 | 28.7 | 85.2 | 224.5 | 215.6 | 215.6 | NO
| NG | 24 | 15 | 16 | 10 | 2.3 | 13.94 | 50 | 87.4 | 30.4 | 28.9 | 85 | 224.4 | 215.6 | 215.6 | NO
1 | OK | 15 | 17 | 17 | 10 | 32.8 | 10.19 | 50 | 87.4 | 30.4 | 43.9 | 70.1 | 216.7 | 218 | 216.7 | YES
| NG | 15 | 29 | 29 | 4 | 22.9 | 3.75 | 50 | 87.4 | 30.4 | 71.5 | 45 | 200.8 | 219.2 | 200.8 | NO
2 | ** OPTIMAL ** | 17 | 21 | 25 | 5 | 38.9 | 8.33 | 50 | 87.4 | 30.4 | 51.4 | 62.3 | 217.1 | 222.4 | 217.1 | YES
| NG | 29 | 4 | 4 | 4 | 23.8 | 3.75 | 50 | 87.4 | 30.4 | 71.5 | 44.7 | 200.8 | 219.3 | 200.8 | NO
3 | OK | 21 | 25 | 25 | 5 | 38.9 | 7.4 | 50 | 87.4 | 30.4 | 55.3 | 58.8 | 215 | 222.4 | 215 | YES
| NG | 4 | 3 | 3 | 1 | 37.9 | 3.68 | 50 | 87.4 | 30.4 | 71.8 | 44.7 | 200.8 | 219.2 | 200.8 | NO
4 | OK | 25 | 20 | 20 | 9 | 42.9 | 4.87 | 50 | 87.4 | 30.4 | 65.8 | 49.1 | 210.1 | 224.2 | 210.1 | YES
| NG | 3 | 27 | 27 | 1 | 158.6 | 2.56 | 50 | 87.4 | 30.4 | 76.8 | 40.4 | 198.1 | 219.8 | 198.1 | NO
5 | OK | 20 | 19 | 19 | 7 | 47.2 | 3.64 | 50 | 87.4 | 30.4 | 71 | 44.4 | 210.4 | 224.1 | 210.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 47-011437
TR_B (available) | 64-019713
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 87.4
TR_B Baseline Loading% | 30.4
Total Scenarios Evaluated | 11
Feasible Scenarios | 5
--- Optimal Solution ---
Switch Parent Node | 17
Switch Child Node | 21
Tie Node (TR_A side) | 25
Tie Node (TR_B side) | 5
Tie Line Distance (m) | 38.9
Load Transferred (kW) | 8.33
TR_A Loading After (%) | 51.4
TR_B Loading After (%) | 62.3
Minimum Voltage (V) | 217.1