## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 6 | 5 | 16 | 23 | 65.5 | 20.13 | 50 | 87.4 | 15.3 | 5 | 30.8 | 226.9 | 210.4 | 210.4 | YES
2 | OK | 5 | 13 | 16 | 23 | 65.5 | 20.13 | 50 | 87.4 | 15.3 | 5 | 30.8 | 226.9 | 210.4 | 210.4 | YES
3 | OK | 13 | 14 | 16 | 23 | 65.5 | 20.13 | 50 | 87.4 | 15.3 | 5 | 30.7 | 226.9 | 210.4 | 210.4 | YES
4 | OK | 14 | 18 | 16 | 23 | 65.5 | 20.03 | 50 | 87.4 | 15.3 | 5.4 | 30.7 | 226.9 | 210.4 | 210.4 | YES
5 | OK | 18 | 0 | 16 | 23 | 65.5 | 18.36 | 50 | 87.4 | 15.3 | 11.8 | 29.4 | 225.7 | 212.4 | 212.4 | YES
6 | OK | 0 | 1 | 16 | 23 | 65.5 | 16.97 | 50 | 87.4 | 15.3 | 17.1 | 28.3 | 225.2 | 213.2 | 213.2 | YES
7 | OK | 1 | 2 | 16 | 23 | 65.5 | 16.83 | 50 | 87.4 | 15.3 | 17.7 | 28.2 | 225.1 | 213.1 | 213.1 | YES
8 | OK | 2 | 24 | 16 | 23 | 65.5 | 13.99 | 50 | 87.4 | 15.3 | 28.7 | 25.9 | 224.5 | 214.2 | 214.2 | YES
9 | OK | 24 | 15 | 16 | 23 | 65.5 | 13.94 | 50 | 87.4 | 15.3 | 28.9 | 25.9 | 224.4 | 214.2 | 214.2 | YES
10 | OK | 15 | 17 | 17 | 6 | 91.8 | 10.19 | 50 | 87.4 | 15.3 | 43.9 | 22.9 | 216.7 | 217.3 | 216.7 | YES
| NG | 15 | 29 | 3 | 22 | 77.8 | 3.75 | 50 | 87.4 | 15.3 | 71.5 | 18.1 | 200.8 | 217.3 | 200.8 | NO
11 | ** OPTIMAL ** | 17 | 21 | 21 | 0 | 100.1 | 8.33 | 50 | 87.4 | 15.3 | 51.4 | 21.4 | 217.1 | 217.3 | 217.1 | YES
| NG | 29 | 4 | 3 | 22 | 77.8 | 3.75 | 50 | 87.4 | 15.3 | 71.5 | 18.1 | 200.8 | 217.3 | 200.8 | NO
12 | OK | 21 | 25 | 25 | 1 | 113.4 | 7.4 | 50 | 87.4 | 15.3 | 55.3 | 20.7 | 215 | 217.3 | 215 | YES
| NG | 4 | 3 | 3 | 22 | 77.8 | 3.68 | 50 | 87.4 | 15.3 | 71.8 | 18.1 | 200.8 | 217.3 | 200.8 | NO
13 | OK | 25 | 20 | 20 | 1 | 134.7 | 4.87 | 50 | 87.4 | 15.3 | 65.8 | 18.9 | 210.1 | 217.6 | 210.1 | YES
| NG | 3 | 27 | 27 | 21 | 80.7 | 2.56 | 50 | 87.4 | 15.3 | 76.8 | 17.3 | 198.1 | 217.3 | 198.1 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 47-011437
TR_B (available) | 67-007033
TR_A Rated kVA | 30
TR_B Rated kVA | 160
TR_A Baseline Loading% | 87.4
TR_B Baseline Loading% | 15.3
Total Scenarios Evaluated | 17
Feasible Scenarios | 13
--- Optimal Solution ---
Switch Parent Node | 17
Switch Child Node | 21
Tie Node (TR_A side) | 21
Tie Node (TR_B side) | 0
Tie Line Distance (m) | 100.1
Load Transferred (kW) | 8.33
TR_A Loading After (%) | 51.4
TR_B Loading After (%) | 21.4
Minimum Voltage (V) | 217.1