## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 28 | 16 | 35 | 47 | 121.1 | 6.94 | 50 | 80.7 | 37.6 | 53.5 | 46.6 | 216 | 202.1 | 202.1 | NO
| NG | 16 | 17 | 35 | 47 | 121.1 | 6.94 | 50 | 80.7 | 37.6 | 53.5 | 46.6 | 216 | 202.1 | 202.1 | NO
| NG | 17 | 4 | 35 | 47 | 121.1 | 6.94 | 50 | 80.7 | 37.6 | 53.5 | 46.6 | 216 | 202.1 | 202.1 | NO
1 | ** OPTIMAL ** | 4 | 15 | 35 | 47 | 121.1 | 1.4 | 50 | 80.7 | 37.6 | 73.9 | 39.2 | 211.8 | 221.3 | 211.8 | YES
2 | OK | 15 | 20 | 35 | 47 | 121.1 | 1.14 | 50 | 80.7 | 37.6 | 76.2 | 38.9 | 211.3 | 222 | 211.3 | YES
3 | OK | 20 | 25 | 35 | 47 | 121.1 | 1.05 | 50 | 80.7 | 37.6 | 76.5 | 38.8 | 211.2 | 222.3 | 211.2 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 47-012199
TR_B (available) | 50-005683
TR_A Rated kVA | 30
TR_B Rated kVA | 100
TR_A Baseline Loading% | 80.7
TR_B Baseline Loading% | 37.6
Total Scenarios Evaluated | 6
Feasible Scenarios | 3
--- Optimal Solution ---
Switch Parent Node | 4
Switch Child Node | 15
Tie Node (TR_A side) | 35
Tie Node (TR_B side) | 47
Tie Line Distance (m) | 121.1
Load Transferred (kW) | 1.4
TR_A Loading After (%) | 73.9
TR_B Loading After (%) | 39.2
Minimum Voltage (V) | 211.8