## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 28 | 5 | 18 | 0 | 1.5 | 5.07 | 50 | 80.7 | 29.6 | 61 | 53.7 | 213.9 | 182.8 | 182.8 | NO
1 | OK | 5 | 6 | 21 | 4 | 1.5 | 5.07 | 50 | 80.7 | 29.6 | 61 | 49.8 | 213.9 | 210.8 | 210.8 | YES
2 | OK | 6 | 12 | 21 | 4 | 1.5 | 4.52 | 50 | 80.7 | 29.6 | 63.1 | 47.5 | 213.5 | 211.3 | 211.3 | YES
3 | OK | 12 | 8 | 21 | 4 | 1.5 | 4.12 | 50 | 80.7 | 29.6 | 64.7 | 45.9 | 213.2 | 211.6 | 211.6 | YES
4 | OK | 8 | 7 | 21 | 4 | 1.5 | 3.79 | 50 | 80.7 | 29.6 | 65.9 | 44.6 | 212.9 | 211.9 | 211.9 | YES
5 | ** OPTIMAL ** | 7 | 14 | 21 | 4 | 1.5 | 3.33 | 50 | 80.7 | 29.6 | 67.7 | 42.7 | 212.5 | 212.3 | 212.3 | YES
6 | OK | 14 | 13 | 21 | 4 | 1.5 | 0.38 | 50 | 80.7 | 29.6 | 78.3 | 31.1 | 210.3 | 214.6 | 210.3 | YES
7 | OK | 13 | 26 | 21 | 4 | 1.5 | 0.38 | 50 | 80.7 | 29.6 | 79.2 | 31.1 | 210.1 | 214.6 | 210.1 | YES
| NG | 26 | 27 | 21 | 4 | 1.5 | 0.24 | 50 | 80.7 | 29.6 | 79.8 | 30.6 | 210 | 214.7 | 210 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 47-012199
TR_B (available) | 59-006822
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 80.7
TR_B Baseline Loading% | 29.6
Total Scenarios Evaluated | 9
Feasible Scenarios | 7
--- Optimal Solution ---
Switch Parent Node | 7
Switch Child Node | 14
Tie Node (TR_A side) | 21
Tie Node (TR_B side) | 4
Tie Line Distance (m) | 1.5
Load Transferred (kW) | 3.33
TR_A Loading After (%) | 67.7
TR_B Loading After (%) | 42.7
Minimum Voltage (V) | 212.3