## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 4 | 3 | 2 | 41 | 102.8 | 2.04 | 50 | 80.7 | 60.4 | 72.6 | 68.3 | 211.9 | 212.6 | 211.9 | YES
2 | OK | 4 | 15 | 35 | 4 | 135.1 | 1.4 | 50 | 80.7 | 60.4 | 73.9 | 66.1 | 211.8 | 210.5 | 210.5 | YES
3 | ** OPTIMAL ** | 4 | 0 | 0 | 41 | 34.9 | 3.2 | 50 | 80.7 | 60.4 | 68 | 72.8 | 213 | 212.7 | 212.7 | YES
4 | OK | 3 | 2 | 2 | 41 | 102.8 | 1.29 | 50 | 80.7 | 60.4 | 75.6 | 65.4 | 210.9 | 212.6 | 210.9 | YES
5 | OK | 15 | 20 | 35 | 4 | 135.1 | 1.14 | 50 | 80.7 | 60.4 | 76.2 | 65.1 | 211.3 | 210.9 | 210.9 | YES
6 | OK | 0 | 1 | 1 | 41 | 66.8 | 1.32 | 50 | 80.7 | 60.4 | 75.4 | 65.5 | 211.4 | 212.6 | 211.4 | YES
7 | OK | 20 | 25 | 35 | 4 | 135.1 | 1.05 | 50 | 80.7 | 60.4 | 76.5 | 64.7 | 211.2 | 211 | 211 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 47-012199
TR_B (available) | 60-019675
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 80.7
TR_B Baseline Loading% | 60.4
Total Scenarios Evaluated | 7
Feasible Scenarios | 7
--- Optimal Solution ---
Switch Parent Node | 4
Switch Child Node | 0
Tie Node (TR_A side) | 0
Tie Node (TR_B side) | 41
Tie Line Distance (m) | 34.9
Load Transferred (kW) | 3.2
TR_A Loading After (%) | 68
TR_B Loading After (%) | 72.8
Minimum Voltage (V) | 212.7