## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 15 | 16 | 37 | 91 | 4.6 | 27.27 | 50 | 129.4 | 48.1 | 10 | 58.5 | 229.3 | 217.7 | 217.7 | YES
2 | OK | 16 | 8 | 37 | 91 | 4.6 | 25.08 | 50 | 129.4 | 48.1 | 18.4 | 55.9 | 228.7 | 217.7 | 217.7 | YES
3 | OK | 8 | 1 | 24 | 2 | 6.3 | 23.14 | 50 | 129.4 | 48.1 | 27.7 | 54.6 | 227.3 | 217.1 | 217.1 | YES
4 | ** OPTIMAL ** | 1 | 0 | 24 | 2 | 6.3 | 21.96 | 50 | 129.4 | 48.1 | 32.2 | 53.2 | 226.2 | 217.7 | 217.7 | YES
5 | OK | 0 | 2 | 24 | 2 | 6.3 | 21.33 | 50 | 129.4 | 48.1 | 34.6 | 52.5 | 225.7 | 217.7 | 217.7 | YES
| NG | 2 | 6 | 6 | 7 | 35.7 | 21.29 | 50 | 129.4 | 48.1 | 34.8 | 76.1 | 225.6 | 188.7 | 188.7 | NO
| NG | 6 | 5 | 27 | 101 | 40.5 | 20.81 | 50 | 129.4 | 48.1 | 36.6 | 72.4 | 225.2 | 185.2 | 185.2 | NO
| NG | 5 | 28 | 27 | 101 | 40.5 | 20.81 | 50 | 129.4 | 48.1 | 36.6 | 72.3 | 225.2 | 185.3 | 185.3 | NO
| NG | 28 | 22 | 27 | 101 | 40.5 | 18.77 | 50 | 129.4 | 48.1 | 44.5 | 72.3 | 221.9 | 185.3 | 185.3 | NO
| NG | 22 | 23 | 27 | 101 | 40.5 | 17.54 | 50 | 129.4 | 48.1 | 49.4 | 72.3 | 219.7 | 185.3 | 185.3 | NO
| NG | 23 | 27 | 27 | 101 | 40.5 | 17.54 | 50 | 129.4 | 48.1 | 49.4 | 72.3 | 219.7 | 185.3 | 185.3 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 47-012366
TR_B (available) | 59-021223
TR_A Rated kVA | 30
TR_B Rated kVA | 100
TR_A Baseline Loading% | 129.4
TR_B Baseline Loading% | 48.1
Total Scenarios Evaluated | 11
Feasible Scenarios | 5
--- Optimal Solution ---
Switch Parent Node | 1
Switch Child Node | 0
Tie Node (TR_A side) | 24
Tie Node (TR_B side) | 2
Tie Line Distance (m) | 6.3
Load Transferred (kW) | 21.96
TR_A Loading After (%) | 32.2
TR_B Loading After (%) | 53.2
Minimum Voltage (V) | 217.7