## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | ** OPTIMAL ** | 18 | 30 | 38 | 18 | 181.9 | 12.07 | 50 | 93.7 | 37.7 | 45 | 37.7 | 218.6 | 218.2 | 218.2 | YES
| NG | 18 | 17 | 45 | 18 | 183.8 | 6.76 | 50 | 93.7 | 37.7 | 19 | 59 | 223.1 | 192.4 | 192.4 | NO
2 | OK | 30 | 32 | 38 | 18 | 181.9 | 10.55 | 50 | 93.7 | 37.7 | 50.8 | 37.7 | 217.5 | 218.2 | 217.5 | YES
| NG | 17 | 16 | 45 | 18 | 183.8 | 6.76 | 50 | 93.7 | 37.7 | 24.7 | 59 | 222 | 192.4 | 192.4 | NO
3 | OK | 32 | 33 | 38 | 18 | 181.9 | 8.09 | 50 | 93.7 | 37.7 | 60.5 | 37.7 | 213.8 | 218.2 | 213.8 | YES
| NG | 16 | 15 | 45 | 18 | 183.8 | 5.66 | 50 | 93.7 | 37.7 | 28.9 | 53.6 | 221.2 | 200.8 | 200.8 | NO
| NG | 15 | 14 | 45 | 18 | 183.8 | 4.81 | 50 | 93.7 | 37.7 | 32.2 | 53.6 | 221.2 | 200.8 | 200.8 | NO
| NG | 14 | 40 | 45 | 18 | 183.8 | 4.81 | 50 | 93.7 | 37.7 | 41.7 | 53.6 | 219.4 | 200.8 | 200.8 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 47-012367
TR_B (available) | 45-013886
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 93.7
TR_B Baseline Loading% | 37.7
Total Scenarios Evaluated | 8
Feasible Scenarios | 3
--- Optimal Solution ---
Switch Parent Node | 18
Switch Child Node | 30
Tie Node (TR_A side) | 38
Tie Node (TR_B side) | 18
Tie Line Distance (m) | 181.9
Load Transferred (kW) | 12.07
TR_A Loading After (%) | 45
TR_B Loading After (%) | 37.7
Minimum Voltage (V) | 218.2