## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 9 | 8 | 30 | 32 | 80.5 | 13.39 | 50 | 82 | 29.3 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 9 | 10 | 10 | 32 | 44.8 | 7.9 | 50 | 82 | 29.3 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 8 | 2 | 30 | 32 | 80.5 | 13.39 | 50 | 82 | 29.3 | 30.4 | 57.5 | 222.4 | 215.3 | 215.3 | YES
2 | OK | 10 | 15 | 15 | 32 | 46.4 | 6.44 | 50 | 82 | 29.3 | 57.1 | 54.2 | 221.6 | 220 | 220 | YES
3 | OK | 2 | 3 | 30 | 32 | 80.5 | 9.56 | 50 | 82 | 29.3 | 45.1 | 54.8 | 220.1 | 216.6 | 216.6 | YES
4 | OK | 2 | 23 | 21 | 10 | 87.1 | 1.32 | 50 | 82 | 29.3 | 76.9 | 34.3 | 218.3 | 225.3 | 218.3 | YES
5 | OK | 2 | 24 | 25 | 35 | 191.4 | 2.11 | 50 | 82 | 29.3 | 73.9 | 37.5 | 219.4 | 223 | 219.4 | YES
6 | ** OPTIMAL ** | 15 | 13 | 13 | 32 | 61.1 | 5.13 | 50 | 82 | 29.3 | 62.1 | 49.1 | 221.6 | 221.9 | 221.6 | YES
7 | OK | 3 | 6 | 30 | 32 | 80.5 | 7.25 | 50 | 82 | 29.3 | 53.9 | 52 | 218.9 | 217.8 | 217.8 | YES
8 | OK | 23 | 22 | 21 | 10 | 87.1 | 0.81 | 50 | 82 | 29.3 | 78.9 | 32.4 | 218.3 | 225.7 | 218.3 | YES
9 | OK | 24 | 25 | 25 | 35 | 191.4 | 1.37 | 50 | 82 | 29.3 | 76.7 | 34.6 | 218.9 | 224.8 | 218.9 | YES
10 | OK | 24 | 26 | 26 | 35 | 225 | 0.74 | 50 | 82 | 29.3 | 79.1 | 32.1 | 218.4 | 225.8 | 218.4 | YES
11 | OK | 13 | 14 | 14 | 11 | 63.9 | 4.71 | 50 | 82 | 29.3 | 63.7 | 47.4 | 221.5 | 223.5 | 221.5 | YES
12 | OK | 6 | 7 | 30 | 32 | 80.5 | 6.18 | 50 | 82 | 29.3 | 58 | 51.9 | 218.1 | 217.8 | 217.8 | YES
13 | OK | 22 | 21 | 21 | 10 | 87.1 | 0.81 | 50 | 82 | 29.3 | 78.9 | 29.3 | 218.3 | 225.8 | 218.3 | YES
14 | OK | 14 | 16 | 16 | 11 | 65.4 | 4.71 | 50 | 82 | 29.3 | 63.7 | 47.4 | 221.5 | 223.8 | 221.5 | YES
15 | OK | 7 | 27 | 30 | 32 | 80.5 | 6.18 | 50 | 82 | 29.3 | 58 | 51.9 | 218.1 | 217.8 | 217.8 | YES
16 | OK | 16 | 17 | 17 | 11 | 67.9 | 2.63 | 50 | 82 | 29.3 | 71.7 | 39.4 | 220.8 | 225.1 | 220.8 | YES
17 | OK | 27 | 4 | 4 | 32 | 147.1 | 2.31 | 50 | 82 | 29.3 | 72.9 | 38.2 | 217.8 | 223.4 | 217.8 | YES
18 | OK | 27 | 29 | 30 | 32 | 80.5 | 3.5 | 50 | 82 | 29.3 | 68.3 | 42.8 | 217.8 | 222.7 | 217.8 | YES
19 | OK | 17 | 34 | 34 | 10 | 96.9 | 2.35 | 50 | 82 | 29.3 | 72.8 | 38.3 | 220.6 | 225.5 | 220.6 | YES
20 | OK | 4 | 5 | 5 | 32 | 149 | 1.84 | 50 | 82 | 29.3 | 74.8 | 36.4 | 217.8 | 224.2 | 217.8 | YES
21 | OK | 29 | 30 | 30 | 32 | 80.5 | 0.87 | 50 | 82 | 29.3 | 78.6 | 32.6 | 217.8 | 225.2 | 217.8 | YES
22 | OK | 34 | 19 | 11 | 24 | 106.4 | 1.27 | 50 | 82 | 29.3 | 77 | 34.2 | 220 | 225.5 | 220 | YES
23 | OK | 5 | 28 | 28 | 32 | 200.5 | 1.84 | 50 | 82 | 29.3 | 74.8 | 36.4 | 217.8 | 224.3 | 217.8 | YES
24 | OK | 19 | 18 | 11 | 24 | 106.4 | 1.27 | 50 | 82 | 29.3 | 77 | 34.2 | 220 | 225.5 | 220 | YES
25 | OK | 18 | 12 | 11 | 24 | 106.4 | 0.89 | 50 | 82 | 29.3 | 78.5 | 32.7 | 219.9 | 225.8 | 219.9 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 47-012716
TR_B (available) | 45-019912
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 82
TR_B Baseline Loading% | 29.3
Total Scenarios Evaluated | 27
Feasible Scenarios | 25
--- Optimal Solution ---
Switch Parent Node | 15
Switch Child Node | 13
Tie Node (TR_A side) | 13
Tie Node (TR_B side) | 32
Tie Line Distance (m) | 61.1
Load Transferred (kW) | 5.13
TR_A Loading After (%) | 62.1
TR_B Loading After (%) | 49.1
Minimum Voltage (V) | 221.6