## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 9 | 10 | 10 | 12 | 44.6 | 7.9 | 50 | 82 | 46.9 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 10 | 15 | 15 | 12 | 46.3 | 6.44 | 50 | 82 | 46.9 | 57.1 | 72.6 | 221.6 | 213.2 | 213.2 | YES
2 | OK | 2 | 3 | 30 | 3 | 37.4 | 9.56 | 50 | 82 | 46.9 | 45.1 | 73.5 | 220.1 | 210.5 | 210.5 | YES
3 | OK | 2 | 23 | 23 | 12 | 101.3 | 1.32 | 50 | 82 | 46.9 | 76.9 | 52.1 | 218.3 | 221.7 | 218.3 | YES
4 | OK | 15 | 13 | 13 | 12 | 61.1 | 5.13 | 50 | 82 | 46.9 | 62.1 | 67.3 | 221.6 | 216.2 | 216.2 | YES
5 | OK | 3 | 6 | 30 | 3 | 37.4 | 7.25 | 50 | 82 | 46.9 | 53.9 | 70.6 | 218.9 | 211.9 | 211.9 | YES
6 | OK | 23 | 22 | 22 | 12 | 122.1 | 0.81 | 50 | 82 | 46.9 | 78.9 | 50.1 | 218.3 | 222.9 | 218.3 | YES
7 | OK | 13 | 14 | 14 | 12 | 68.4 | 4.71 | 50 | 82 | 46.9 | 63.7 | 65.6 | 221.5 | 217.2 | 217.2 | YES
8 | OK | 6 | 7 | 30 | 3 | 37.4 | 6.18 | 50 | 82 | 46.9 | 58 | 70.5 | 218.1 | 212 | 212 | YES
9 | OK | 22 | 21 | 21 | 12 | 123.6 | 0.81 | 50 | 82 | 46.9 | 78.9 | 46.9 | 218.3 | 223.2 | 218.3 | YES
10 | OK | 14 | 16 | 16 | 12 | 82.9 | 4.71 | 50 | 82 | 46.9 | 63.7 | 65.6 | 221.5 | 217.4 | 217.4 | YES
11 | OK | 7 | 27 | 30 | 3 | 37.4 | 6.18 | 50 | 82 | 46.9 | 58 | 70.5 | 218.1 | 212 | 212 | YES
12 | OK | 16 | 17 | 17 | 12 | 89.4 | 2.63 | 50 | 82 | 46.9 | 71.7 | 57.3 | 220.8 | 219.5 | 219.5 | YES
13 | OK | 27 | 4 | 4 | 5 | 101.2 | 2.31 | 50 | 82 | 46.9 | 72.9 | 56.1 | 217.8 | 220 | 217.8 | YES
14 | OK | 27 | 29 | 30 | 3 | 37.4 | 3.5 | 50 | 82 | 46.9 | 68.3 | 61 | 217.8 | 217.6 | 217.6 | YES
15 | OK | 17 | 34 | 34 | 12 | 115 | 2.35 | 50 | 82 | 46.9 | 72.8 | 56.2 | 220.6 | 219.5 | 219.5 | YES
16 | OK | 4 | 5 | 5 | 5 | 101.7 | 1.84 | 50 | 82 | 46.9 | 74.8 | 54.2 | 217.8 | 220.7 | 217.8 | YES
17 | OK | 29 | 30 | 30 | 3 | 37.4 | 0.87 | 50 | 82 | 46.9 | 78.6 | 50.4 | 217.8 | 221.9 | 217.8 | YES
18 | OK | 34 | 19 | 19 | 12 | 124.1 | 1.27 | 50 | 82 | 46.9 | 77 | 51.9 | 220 | 222.2 | 220 | YES
19 | OK | 5 | 28 | 28 | 0 | 109.8 | 1.84 | 50 | 82 | 46.9 | 74.8 | 54.1 | 217.8 | 221 | 217.8 | YES
20 | ** OPTIMAL ** | 19 | 18 | 18 | 12 | 147.1 | 1.27 | 50 | 82 | 46.9 | 77 | 51.9 | 220 | 222.2 | 220 | YES
21 | OK | 28 | 31 | 31 | 17 | 144.9 | 0.73 | 50 | 82 | 46.9 | 79.1 | 49.7 | 217.8 | 222.7 | 217.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 47-012716
TR_B (available) | 65-009967
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 82
TR_B Baseline Loading% | 46.9
Total Scenarios Evaluated | 22
Feasible Scenarios | 21
--- Optimal Solution ---
Switch Parent Node | 19
Switch Child Node | 18
Tie Node (TR_A side) | 18
Tie Node (TR_B side) | 12
Tie Line Distance (m) | 147.1
Load Transferred (kW) | 1.27
TR_A Loading After (%) | 77
TR_B Loading After (%) | 51.9
Minimum Voltage (V) | 220