## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 9 | 8 | 30 | 0 | 126.2 | 13.39 | 50 | 82 | 6.2 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 9 | 10 | 0 | 0 | 1 | 7.9 | 50 | 82 | 6.2 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 8 | 2 | 30 | 0 | 126.2 | 13.39 | 50 | 82 | 6.2 | 30.4 | 34.9 | 222.4 | 213.6 | 213.6 | YES
2 | OK | 10 | 15 | 0 | 0 | 1 | 6.44 | 50 | 82 | 6.2 | 57.1 | 12.7 | 221.6 | 226.5 | 221.6 | YES
3 | OK | 2 | 3 | 30 | 0 | 126.2 | 9.56 | 50 | 82 | 6.2 | 45.1 | 32.1 | 220.1 | 215.2 | 215.2 | YES
4 | ** OPTIMAL ** | 15 | 13 | 0 | 0 | 1 | 5.13 | 50 | 82 | 6.2 | 62.1 | 12.7 | 221.6 | 226.5 | 221.6 | YES
5 | OK | 3 | 6 | 30 | 0 | 126.2 | 7.25 | 50 | 82 | 6.2 | 53.9 | 29.2 | 218.9 | 216.8 | 216.8 | YES
6 | OK | 13 | 14 | 14 | 0 | 105.5 | 4.71 | 50 | 82 | 6.2 | 63.7 | 12.4 | 221.5 | 226.7 | 221.5 | YES
7 | OK | 6 | 7 | 30 | 0 | 126.2 | 6.18 | 50 | 82 | 6.2 | 58 | 29.1 | 218.1 | 216.9 | 216.9 | YES
8 | OK | 14 | 16 | 16 | 0 | 128.3 | 4.71 | 50 | 82 | 6.2 | 63.7 | 12.4 | 221.5 | 226.7 | 221.5 | YES
9 | OK | 7 | 27 | 30 | 0 | 126.2 | 6.18 | 50 | 82 | 6.2 | 58 | 29.1 | 218.1 | 216.9 | 216.9 | YES
10 | OK | 16 | 17 | 17 | 0 | 137.4 | 2.63 | 50 | 82 | 6.2 | 71.7 | 8.4 | 220.8 | 227.5 | 220.8 | YES
11 | OK | 27 | 29 | 30 | 0 | 126.2 | 3.5 | 50 | 82 | 6.2 | 68.3 | 19.8 | 217.8 | 222.9 | 217.8 | YES
12 | OK | 17 | 34 | 34 | 0 | 137.9 | 2.35 | 50 | 82 | 6.2 | 72.8 | 7.3 | 220.6 | 227.7 | 220.6 | YES
13 | OK | 29 | 30 | 30 | 0 | 126.2 | 0.87 | 50 | 82 | 6.2 | 78.6 | 9.5 | 217.8 | 227.3 | 217.8 | YES
14 | OK | 34 | 19 | 19 | 0 | 138 | 1.27 | 50 | 82 | 6.2 | 77 | 7.3 | 220 | 227.7 | 220 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 47-012716
TR_B (available) | 66-004355
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 82
TR_B Baseline Loading% | 6.2
Total Scenarios Evaluated | 16
Feasible Scenarios | 14
--- Optimal Solution ---
Switch Parent Node | 15
Switch Child Node | 13
Tie Node (TR_A side) | 0
Tie Node (TR_B side) | 0
Tie Line Distance (m) | 1
Load Transferred (kW) | 5.13
TR_A Loading After (%) | 62.1
TR_B Loading After (%) | 12.7
Minimum Voltage (V) | 221.6