## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 18 | 17 | 39 | 72 | 24.5 | 12.72 | 50 | 87.7 | 53.6 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 17 | 16 | 39 | 72 | 24.5 | 11.71 | 50 | 87.7 | 53.6 | 42.6 | 60.9 | 222.2 | 210.2 | 210.2 | YES
2 | OK | 16 | 23 | 39 | 72 | 24.5 | 9.92 | 50 | 87.7 | 53.6 | 49.5 | 60.3 | 221.3 | 211.5 | 211.5 | YES
3 | ** OPTIMAL ** | 23 | 14 | 39 | 72 | 24.5 | 5.59 | 50 | 87.7 | 53.6 | 66.1 | 57.8 | 219.5 | 215.2 | 215.2 | YES
4 | OK | 14 | 15 | 39 | 72 | 24.5 | 3.27 | 50 | 87.7 | 53.6 | 75 | 55.5 | 219.2 | 215.2 | 215.2 | YES
5 | OK | 15 | 31 | 39 | 72 | 24.5 | 2.92 | 50 | 87.7 | 53.6 | 76.3 | 55.5 | 218.9 | 215.2 | 215.2 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 47-012851
TR_B (available) | 54-008208
TR_A Rated kVA | 30
TR_B Rated kVA | 100
TR_A Baseline Loading% | 87.7
TR_B Baseline Loading% | 53.6
Total Scenarios Evaluated | 6
Feasible Scenarios | 5
--- Optimal Solution ---
Switch Parent Node | 23
Switch Child Node | 14
Tie Node (TR_A side) | 39
Tie Node (TR_B side) | 72
Tie Line Distance (m) | 24.5
Load Transferred (kW) | 5.59
TR_A Loading After (%) | 66.1
TR_B Loading After (%) | 57.8
Minimum Voltage (V) | 215.2