## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 18 | 17 | 11 | 0 | 2.8 | 12.72 | 50 | 87.7 | 35.7 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 18 | 19 | 19 | 30 | 133.7 | 10.06 | 50 | 87.7 | 35.7 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 17 | 16 | 11 | 0 | 2.8 | 11.71 | 50 | 87.7 | 35.7 | 42.6 | 49.8 | 222.2 | 217.2 | 217.2 | YES
2 | OK | 19 | 20 | 20 | 30 | 142.5 | 8.56 | 50 | 87.7 | 35.7 | 54.6 | 41 | 222.9 | 212.6 | 212.6 | YES
3 | OK | 16 | 23 | 11 | 0 | 2.8 | 9.92 | 50 | 87.7 | 35.7 | 49.5 | 47.5 | 221.3 | 218.2 | 218.2 | YES
4 | OK | 20 | 21 | 21 | 30 | 145.9 | 8.13 | 50 | 87.7 | 35.7 | 56.2 | 40.5 | 222.7 | 213.6 | 213.6 | YES
5 | OK | 23 | 14 | 41 | 74 | 48.7 | 5.59 | 50 | 87.7 | 35.7 | 66.1 | 42.6 | 219.5 | 212.1 | 212.1 | YES
6 | ** OPTIMAL ** | 23 | 12 | 11 | 0 | 2.8 | 3.73 | 50 | 87.7 | 35.7 | 73.3 | 40.1 | 219.4 | 219.5 | 219.4 | YES
7 | OK | 14 | 15 | 41 | 74 | 48.7 | 3.27 | 50 | 87.7 | 35.7 | 75 | 39.6 | 219.2 | 219 | 219 | YES
8 | OK | 15 | 31 | 41 | 74 | 48.7 | 2.92 | 50 | 87.7 | 35.7 | 76.3 | 39.2 | 218.9 | 219.5 | 218.9 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 47-012851
TR_B (available) | 65-018165
TR_A Rated kVA | 30
TR_B Rated kVA | 100
TR_A Baseline Loading% | 87.7
TR_B Baseline Loading% | 35.7
Total Scenarios Evaluated | 10
Feasible Scenarios | 8
--- Optimal Solution ---
Switch Parent Node | 23
Switch Child Node | 12
Tie Node (TR_A side) | 11
Tie Node (TR_B side) | 0
Tie Line Distance (m) | 2.8
Load Transferred (kW) | 3.73
TR_A Loading After (%) | 73.3
TR_B Loading After (%) | 40.1
Minimum Voltage (V) | 219.4