## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 21 | 22 | 42 | 0 | 2.2 | 4.64 | 50 | 80.6 | 8.3 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 21 | 23 | 46 | 0 | 89 | 16.32 | 50 | 80.6 | 8.3 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 22 | 24 | 42 | 0 | 2.2 | 3.61 | 50 | 80.6 | 8.3 | 66.8 | 16.6 | 219.3 | 221.3 | 219.3 | YES
2 | OK | 22 | 25 | 25 | 0 | 106.2 | 1.03 | 50 | 80.6 | 8.3 | 76.7 | 10.7 | 218.8 | 222.2 | 218.8 | YES
3 | OK | 23 | 20 | 46 | 0 | 89 | 15.47 | 50 | 80.6 | 8.3 | 21 | 35.2 | 226.1 | 210.3 | 210.3 | YES
4 | OK | 24 | 28 | 42 | 0 | 2.2 | 3.55 | 50 | 80.6 | 8.3 | 67 | 16.5 | 219.3 | 221.3 | 219.3 | YES
5 | OK | 25 | 26 | 26 | 6 | 110.8 | 0.73 | 50 | 80.6 | 8.3 | 77.8 | 10 | 218.8 | 222.3 | 218.8 | YES
6 | OK | 20 | 14 | 14 | 0 | 152.4 | 6.05 | 50 | 80.6 | 8.3 | 55 | 22.5 | 220.7 | 219.9 | 219.9 | YES
7 | OK | 20 | 32 | 46 | 0 | 89 | 4.12 | 50 | 80.6 | 8.3 | 64.7 | 17.9 | 220.6 | 222.7 | 220.6 | YES
8 | OK | 20 | 18 | 18 | 0 | 148.1 | 4.7 | 50 | 80.6 | 8.3 | 62.3 | 19.4 | 220.6 | 222.7 | 220.6 | YES
9 | OK | 28 | 29 | 42 | 0 | 2.2 | 2.63 | 50 | 80.6 | 8.3 | 70.5 | 14.4 | 219.3 | 221.8 | 219.3 | YES
10 | OK | 32 | 39 | 46 | 0 | 89 | 2.73 | 50 | 80.6 | 8.3 | 70 | 14.7 | 220.6 | 222.7 | 220.6 | YES
11 | OK | 18 | 19 | 19 | 7 | 150.6 | 4.7 | 50 | 80.6 | 8.3 | 62.3 | 19.3 | 220.6 | 222.7 | 220.6 | YES
12 | OK | 29 | 38 | 42 | 0 | 2.2 | 2.05 | 50 | 80.6 | 8.3 | 72.7 | 13 | 219 | 221.8 | 219 | YES
13 | ** OPTIMAL ** | 39 | 33 | 46 | 0 | 89 | 2.73 | 50 | 80.6 | 8.3 | 70 | 14.7 | 220.6 | 222.7 | 220.6 | YES
14 | OK | 19 | 52 | 52 | 5 | 155.8 | 4.51 | 50 | 80.6 | 8.3 | 63.1 | 18.8 | 220.6 | 222.9 | 220.6 | YES
15 | OK | 38 | 42 | 42 | 0 | 2.2 | 1.31 | 50 | 80.6 | 8.3 | 75.6 | 10.9 | 219 | 222.2 | 219 | YES
16 | OK | 33 | 31 | 46 | 0 | 89 | 0.21 | 50 | 80.6 | 8.3 | 79.8 | 8.8 | 219 | 222.7 | 219 | YES
17 | OK | 42 | 41 | 41 | 0 | 9.5 | 0.41 | 50 | 80.6 | 8.3 | 79 | 9.3 | 218.8 | 222.5 | 218.8 | YES
18 | OK | 42 | 44 | 44 | 0 | 14.7 | 0.9 | 50 | 80.6 | 8.3 | 77.1 | 10 | 219 | 222.4 | 219 | YES
19 | OK | 31 | 30 | 46 | 0 | 89 | 0.19 | 50 | 80.6 | 8.3 | 79.8 | 8.8 | 219 | 222.7 | 219 | YES
20 | OK | 41 | 37 | 37 | 0 | 96.1 | 0.41 | 50 | 80.6 | 8.3 | 79 | 9.3 | 218.8 | 222.5 | 218.8 | YES
21 | OK | 44 | 43 | 43 | 0 | 63.1 | 0.7 | 50 | 80.6 | 8.3 | 77.9 | 10 | 218.8 | 222.4 | 218.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 48-002560
TR_B (available) | 59-002296
TR_A Rated kVA | 30
TR_B Rated kVA | 50
TR_A Baseline Loading% | 80.6
TR_B Baseline Loading% | 8.3
Total Scenarios Evaluated | 23
Feasible Scenarios | 21
--- Optimal Solution ---
Switch Parent Node | 39
Switch Child Node | 33
Tie Node (TR_A side) | 46
Tie Node (TR_B side) | 0
Tie Line Distance (m) | 89
Load Transferred (kW) | 2.73
TR_A Loading After (%) | 70
TR_B Loading After (%) | 14.7
Minimum Voltage (V) | 220.6