## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 0 | 1 | 19 | 6 | 60 | 11.2 | 50 | 85 | 15.7 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 0 | 11 | 11 | 6 | 206.2 | 10.52 | 50 | 85 | 15.7 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 1 | 51 | 19 | 6 | 60 | 10.84 | 50 | 85 | 15.7 | 42.8 | 36.9 | 213.2 | 208.7 | 208.7 | NO
| NG | 11 | 10 | 10 | 6 | 239.2 | 10.52 | 50 | 85 | 15.7 | 43.5 | 64.3 | 220.3 | 174.5 | 174.5 | NO
| NG | 51 | 12 | 19 | 6 | 60 | 10.84 | 50 | 85 | 15.7 | 42.8 | 36.9 | 213.2 | 208.7 | 208.7 | NO
1 | OK | 12 | 13 | 19 | 6 | 60 | 10.05 | 50 | 85 | 15.7 | 45.8 | 33.5 | 213.2 | 211.8 | 211.8 | YES
2 | OK | 13 | 29 | 19 | 6 | 60 | 9.71 | 50 | 85 | 15.7 | 47.1 | 33.2 | 213 | 212.1 | 212.1 | YES
3 | ** OPTIMAL ** | 29 | 54 | 19 | 6 | 60 | 8.38 | 50 | 85 | 15.7 | 52.2 | 28.4 | 212.8 | 216.5 | 212.8 | YES
4 | OK | 54 | 35 | 35 | 6 | 167.1 | 3.94 | 50 | 85 | 15.7 | 69.4 | 31.8 | 211.8 | 212.1 | 211.8 | YES
| NG | 54 | 30 | 30 | 6 | 150.1 | 4.01 | 50 | 85 | 15.7 | 69.3 | 31.5 | 209.6 | 217.6 | 209.6 | NO
5 | OK | 35 | 36 | 36 | 6 | 192.3 | 3.64 | 50 | 85 | 15.7 | 70.6 | 30.5 | 211.6 | 213.6 | 211.6 | YES
| NG | 30 | 31 | 31 | 6 | 182.4 | 3.02 | 50 | 85 | 15.7 | 73.2 | 27.7 | 208.9 | 218.1 | 208.9 | NO
6 | OK | 36 | 23 | 23 | 6 | 196.9 | 2.64 | 50 | 85 | 15.7 | 74.5 | 26.2 | 210.8 | 218.5 | 210.8 | YES
| NG | 31 | 45 | 45 | 6 | 208.7 | 2.75 | 50 | 85 | 15.7 | 74.2 | 26.6 | 208.9 | 219.2 | 208.9 | NO
7 | OK | 23 | 24 | 24 | 6 | 240.4 | 2.29 | 50 | 85 | 15.7 | 75.9 | 24.8 | 210.5 | 219.8 | 210.5 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 48-004149
TR_B (available) | 45-018889
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 85
TR_B Baseline Loading% | 15.7
Total Scenarios Evaluated | 15
Feasible Scenarios | 7
--- Optimal Solution ---
Switch Parent Node | 29
Switch Child Node | 54
Tie Node (TR_A side) | 19
Tie Node (TR_B side) | 6
Tie Line Distance (m) | 60
Load Transferred (kW) | 8.38
TR_A Loading After (%) | 52.2
TR_B Loading After (%) | 28.4
Minimum Voltage (V) | 212.8