## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 0 | 1 | 49 | 8 | 45 | 11.2 | 50 | 85 | 15.8 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 0 | 11 | 2 | 4 | 6 | 10.52 | 50 | 85 | 15.8 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 1 | 51 | 49 | 8 | 45 | 10.84 | 50 | 85 | 15.8 | 42.8 | 35.9 | 213.2 | 217.8 | 213.2 | YES
2 | OK | 11 | 10 | 2 | 4 | 6 | 10.52 | 50 | 85 | 15.8 | 43.5 | 22.3 | 220.3 | 219.6 | 219.6 | YES
3 | OK | 51 | 12 | 49 | 8 | 45 | 10.84 | 50 | 85 | 15.8 | 42.8 | 35.9 | 213.2 | 217.8 | 213.2 | YES
4 | ** OPTIMAL ** | 10 | 9 | 2 | 4 | 6 | 8.78 | 50 | 85 | 15.8 | 50.1 | 15.8 | 220.2 | 221.7 | 220.2 | YES
5 | OK | 12 | 13 | 49 | 8 | 45 | 10.05 | 50 | 85 | 15.8 | 45.8 | 32.7 | 213.2 | 218.5 | 213.2 | YES
6 | OK | 9 | 55 | 2 | 4 | 6 | 8.68 | 50 | 85 | 15.8 | 50.5 | 15.8 | 220.2 | 221.7 | 220.2 | YES
7 | OK | 13 | 29 | 49 | 8 | 45 | 9.71 | 50 | 85 | 15.8 | 47.1 | 32.5 | 213 | 218.5 | 213 | YES
8 | OK | 55 | 2 | 2 | 4 | 6 | 8.06 | 50 | 85 | 15.8 | 52.9 | 15.8 | 219.7 | 221.7 | 219.7 | YES
9 | OK | 29 | 54 | 49 | 8 | 45 | 8.38 | 50 | 85 | 15.8 | 52.2 | 28 | 212.8 | 219.4 | 212.8 | YES
10 | OK | 2 | 3 | 17 | 17 | 42.4 | 7.74 | 50 | 85 | 15.8 | 54.1 | 46 | 219.5 | 215.1 | 215.1 | YES
| NG | 54 | 30 | 49 | 8 | 45 | 4.01 | 50 | 85 | 15.8 | 69.3 | 26.4 | 209.6 | 219.7 | 209.6 | NO
11 | OK | 3 | 18 | 17 | 17 | 42.4 | 6.82 | 50 | 85 | 15.8 | 57.6 | 42.4 | 218.8 | 215.9 | 215.9 | YES
| NG | 30 | 31 | 49 | 8 | 45 | 3.02 | 50 | 85 | 15.8 | 73.2 | 25.9 | 208.9 | 219.8 | 208.9 | NO
12 | OK | 18 | 53 | 17 | 17 | 42.4 | 6.5 | 50 | 85 | 15.8 | 58.9 | 41.1 | 218.5 | 216.2 | 216.2 | YES
| NG | 31 | 45 | 49 | 8 | 45 | 2.75 | 50 | 85 | 15.8 | 74.2 | 24.8 | 208.9 | 220 | 208.9 | NO
13 | OK | 53 | 52 | 17 | 17 | 42.4 | 5.69 | 50 | 85 | 15.8 | 62 | 38 | 217.9 | 216.9 | 216.9 | YES
14 | OK | 52 | 17 | 17 | 17 | 42.4 | 5.52 | 50 | 85 | 15.8 | 62.7 | 37.3 | 217.8 | 217 | 217 | YES
15 | OK | 17 | 8 | 7 | 10 | 44.1 | 5.35 | 50 | 85 | 15.8 | 63.3 | 36.6 | 217.7 | 217.7 | 217.7 | YES
16 | OK | 8 | 7 | 7 | 10 | 44.1 | 3.69 | 50 | 85 | 15.8 | 69.9 | 30.1 | 216.4 | 219 | 216.4 | YES
17 | OK | 8 | 16 | 16 | 9 | 77.8 | 1.66 | 50 | 85 | 15.8 | 78.1 | 22.2 | 212.4 | 220.5 | 212.4 | YES
18 | OK | 7 | 6 | 6 | 11 | 49 | 3.27 | 50 | 85 | 15.8 | 71.5 | 28.5 | 216 | 219.3 | 216 | YES
19 | OK | 6 | 5 | 5 | 11 | 84.1 | 3.15 | 50 | 85 | 15.8 | 72 | 28 | 215.9 | 219.4 | 215.9 | YES
20 | OK | 5 | 4 | 4 | 11 | 114 | 3.04 | 50 | 85 | 15.8 | 72.4 | 27.6 | 215.8 | 219.5 | 215.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 48-004149
TR_B (available) | 65-027235
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 85
TR_B Baseline Loading% | 15.8
Total Scenarios Evaluated | 25
Feasible Scenarios | 20
--- Optimal Solution ---
Switch Parent Node | 10
Switch Child Node | 9
Tie Node (TR_A side) | 2
Tie Node (TR_B side) | 4
Tie Line Distance (m) | 6
Load Transferred (kW) | 8.78
TR_A Loading After (%) | 50.1
TR_B Loading After (%) | 15.8
Minimum Voltage (V) | 220.2