## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 69 | 73 | 75 | 12 | 92.9 | 1.97 | 50 | 39.6 | 75.7 | 38.6 | 229.9 | 219.2 | 16.1 | 16.1 | NO
| NG | 54 | 50 | 50 | 12 | 129.3 | 1.78 | 50 | 39.6 | 75.7 | 39.6 | 78.1 | 60.6 | 204.4 | 60.6 | NO
| NG | 25 | 26 | 18 | 12 | 93.2 | 4.11 | 50 | 39.6 | 75.7 | 193.1 | 76.1 | 20.9 | 211.5 | 20.9 | NO
1 | OK | 72 | 74 | 74 | 12 | 80.1 | 3.6 | 50 | 39.6 | 75.7 | 39.6 | 75.7 | 218.6 | 212.8 | 212.8 | YES
| NG | 26 | 27 | 18 | 12 | 93.2 | 3.4 | 50 | 39.6 | 75.7 | 0 | 76 | 12.8 | 211.9 | 12.8 | NO
2 | OK | 27 | 28 | 18 | 12 | 93.2 | 2.5 | 50 | 39.6 | 75.7 | 37.4 | 76 | 219.8 | 211.9 | 211.9 | YES
3 | OK | 28 | 29 | 18 | 12 | 93.2 | 2.25 | 50 | 39.6 | 75.7 | 37.5 | 75.8 | 219.7 | 212.5 | 212.5 | YES
4 | ** OPTIMAL ** | 29 | 19 | 18 | 12 | 93.2 | 2.19 | 50 | 39.6 | 75.7 | 37.5 | 75.7 | 219.7 | 212.8 | 212.8 | YES
| NG | 12 | 13 | 23 | 12 | 83.1 | 2.65 | 50 | 39.6 | 75.7 | 0 | 77.8 | 11.9 | 205.5 | 11.9 | NO
| NG | 13 | 14 | 23 | 12 | 83.1 | 0.69 | 50 | 39.6 | 75.7 | 0 | 76.4 | 6 | 210.4 | 6 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 49-000087
TR_B (available) | 49-014732
TR_A Rated kVA | 100
TR_B Rated kVA | 100
TR_A Baseline Loading% | 39.6
TR_B Baseline Loading% | 75.7
Total Scenarios Evaluated | 10
Feasible Scenarios | 4
--- Optimal Solution ---
Switch Parent Node | 29
Switch Child Node | 19
Tie Node (TR_A side) | 18
Tie Node (TR_B side) | 12
Tie Line Distance (m) | 93.2
Load Transferred (kW) | 2.19
TR_A Loading After (%) | 37.5
TR_B Loading After (%) | 75.7
Minimum Voltage (V) | 212.8