## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 60 | 59 | 59 | 42 | 159.6 | 14.66 | 50 | 39.6 | 50.1 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 50.1% (degenerate)
| NG | 60 | 61 | 63 | 88 | 52.6 | 12.46 | 50 | 39.6 | 50.1 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 50.1% (degenerate)
| NG | 59 | 57 | 57 | 42 | 163.1 | 14.66 | 50 | 39.6 | 50.1 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 50.1% (degenerate)
1 | OK | 61 | 67 | 67 | 88 | 133.3 | 3.44 | 50 | 39.6 | 50.1 | 39.6 | 50.1 | 218.6 | 215.8 | 215.8 | YES
| NG | 61 | 68 | 63 | 88 | 52.6 | 9.02 | 50 | 39.6 | 50.1 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 50.1% (degenerate)
| NG | 32 | 6 | 42 | 42 | 33 | 40.71 | 50 | 39.6 | 50.1 | 0 | 81.2 | 23.5 | 195.8 | 23.5 | NO
| NG | 32 | 5 | 37 | 40 | 50 | 18.39 | 50 | 39.6 | 50.1 | 0 | 64 | 5.5 | 212.2 | 5.5 | NO
| NG | 57 | 58 | 58 | 42 | 199.4 | 8.5 | 50 | 39.6 | 50.1 | 35.2 | 17095.4 | 220.5 | 11.9 | 11.9 | NO
2 | OK | 57 | 49 | 3 | 40 | 174.8 | 6.16 | 50 | 39.6 | 50.1 | 36.1 | 54.8 | 219.2 | 215.5 | 215.5 | YES
| NG | 68 | 66 | 63 | 88 | 52.6 | 9.02 | 50 | 39.6 | 50.1 | 37.8 | 1332.9 | 219 | 13.8 | 13.8 | NO
| NG | 6 | 7 | 7 | 42 | 178.5 | 20.92 | 50 | 39.6 | 50.1 | 0 | 66.2 | 12.2 | 209.6 | 12.2 | NO
| NG | 6 | 30 | 30 | 41 | 168.9 | 3.47 | 50 | 39.6 | 50.1 | 37.3 | 51.5 | 47.8 | 215.6 | 47.8 | NO
3 | OK | 6 | 43 | 42 | 42 | 33 | 15.14 | 50 | 39.6 | 50.1 | 31.8 | 61.5 | 220.7 | 215.1 | 215.1 | YES
| NG | 5 | 4 | 37 | 40 | 50 | 18.39 | 50 | 39.6 | 50.1 | [5 empty] | NO | TR_A sim: loading 843% (degenerate)
| NG | 58 | 69 | 69 | 42 | 202.6 | 7.78 | 50 | 39.6 | 50.1 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 50.1% (degenerate)
| NG | 49 | 54 | 54 | 83 | 183 | 4.6 | 50 | 39.6 | 50.1 | 37.4 | 53.6 | 60.8 | 215.6 | 60.8 | NO
| NG | 66 | 64 | 63 | 88 | 52.6 | 5.67 | 50 | 39.6 | 50.1 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 50.1% (degenerate)
| NG | 7 | 8 | 8 | 42 | 205.1 | 18.31 | 50 | 39.6 | 50.1 | 262.6 | 64.1 | 6.3 | 212.9 | 6.3 | NO
| NG | 30 | 31 | 31 | 40 | 173.4 | 2.13 | 50 | 39.6 | 50.1 | 38.2 | 50.5 | 47.6 | 215.8 | 47.6 | NO
4 | OK | 43 | 44 | 44 | 42 | 184.3 | 2.82 | 50 | 39.6 | 50.1 | 38.1 | 52.2 | 219 | 215.7 | 215.7 | YES
5 | OK | 43 | 46 | 42 | 42 | 33 | 12.32 | 50 | 39.6 | 50.1 | 33.2 | 59.4 | 220.3 | 215.3 | 215.3 | YES
6 | OK | 4 | 15 | 15 | 41 | 128.1 | 7.9 | 50 | 39.6 | 50.1 | 36 | 56 | 219.3 | 215.5 | 215.5 | YES
| NG | 4 | 21 | 37 | 40 | 50 | 10.49 | 50 | 39.6 | 50.1 | [5 empty] | NO | TR_A sim: loading 929% (degenerate)
| NG | 54 | 50 | 50 | 82 | 185.8 | 1.78 | 50 | 39.6 | 50.1 | 39.6 | 51.5 | 60.6 | 215.8 | 60.6 | NO
| NG | 64 | 65 | 65 | 88 | 93.9 | 4.23 | 50 | 39.6 | 50.1 | 39.2 | 26.6 | 218.7 | 12.8 | 12.8 | NO
| NG | 64 | 62 | 63 | 88 | 52.6 | 1.44 | 50 | 39.6 | 50.1 | 39.6 | 29.8 | 218.6 | 8.4 | 8.4 | NO
| NG | 8 | 24 | 24 | 42 | 206.8 | 6.39 | 50 | 39.6 | 50.1 | 0 | 55 | 33.9 | 214.9 | 33.9 | NO
7 | OK | 44 | 45 | 45 | 42 | 203.6 | 1.72 | 50 | 39.6 | 50.1 | 38.1 | 51.4 | 219 | 215.7 | 215.7 | YES
8 | OK | 46 | 79 | 42 | 42 | 33 | 7.81 | 50 | 39.6 | 50.1 | 33.2 | 56 | 220.3 | 215.1 | 215.1 | YES
9 | OK | 15 | 17 | 17 | 40 | 131.6 | 6.68 | 50 | 39.6 | 50.1 | 36 | 54.8 | 219.3 | 215.4 | 215.4 | YES
| NG | 21 | 38 | 37 | 40 | 50 | 10.49 | 50 | 39.6 | 50.1 | 145.7 | 58 | 19 | 215.1 | 19 | NO
10 | OK | 65 | 77 | 77 | 82 | 99.5 | 3.82 | 50 | 39.6 | 50.1 | 39.2 | 50.1 | 218.7 | 215.8 | 215.8 | YES
| NG | 62 | 63 | 63 | 88 | 52.6 | 1.1 | 50 | 39.6 | 50.1 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 50.1% (degenerate)
| NG | 24 | 25 | 25 | 41 | 209.8 | 6.39 | 50 | 39.6 | 50.1 | 0 | 55 | 11.3 | 214.7 | 11.3 | NO
11 | OK | 79 | 48 | 42 | 42 | 33 | 3.09 | 50 | 39.6 | 50.1 | 38.7 | 52.4 | 218.8 | 215.8 | 215.8 | YES
12 | OK | 17 | 16 | 16 | 88 | 135.5 | 3.95 | 50 | 39.6 | 50.1 | 37.2 | 53.1 | 219.1 | 215.6 | 215.6 | YES
| NG | 38 | 33 | 37 | 40 | 50 | 9.85 | 50 | 39.6 | 50.1 | 198.8 | 57.5 | 16.6 | 215.1 | 16.6 | NO
| NG | 63 | 78 | 78 | 83 | 57.1 | 0.01 | 50 | 39.6 | 50.1 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 50.1% (degenerate)
13 | ** OPTIMAL ** | 48 | 47 | 42 | 42 | 33 | 2.37 | 50 | 39.6 | 50.1 | 39.6 | 51.9 | 218.6 | 215.9 | 215.9 | YES
14 | OK | 16 | 52 | 52 | 83 | 138.7 | 3.95 | 50 | 39.6 | 50.1 | 37.2 | 53.1 | 219.1 | 215.6 | 215.6 | YES
| NG | 33 | 34 | 37 | 40 | 50 | 4.85 | 50 | 39.6 | 50.1 | 1.7 | 53.7 | 8.9 | 215.7 | 8.9 | NO
| NG | 33 | 39 | 39 | 40 | 90.1 | 5 | 50 | 39.6 | 50.1 | 241.5 | 53.9 | 5.8 | 215.2 | 5.8 | NO
15 | OK | 52 | 53 | 53 | 82 | 141.2 | 1.5 | 50 | 39.6 | 50.1 | 39.1 | 51.2 | 218.7 | 215.8 | 215.8 | YES
| NG | 34 | 37 | 37 | 40 | 50 | 4.03 | 50 | 39.6 | 50.1 | 0 | 53.1 | 25.5 | 215.7 | 25.5 | NO
| NG | 39 | 40 | 40 | 40 | 94 | 1.33 | 50 | 39.6 | 50.1 | 5.7 | 51.1 | 11.9 | 215.7 | 11.9 | NO
| NG | 37 | 35 | 35 | 40 | 52.1 | 3.98 | 50 | 39.6 | 50.1 | 0 | 53.1 | 5.3 | 215.7 | 5.3 | NO
16 | OK | 35 | 36 | 36 | 88 | 54.9 | 1.73 | 50 | 39.6 | 50.1 | 0 | 51.4 | 326.6 | 215.9 | 215.9 | YES
| NG | 36 | 56 | 56 | 83 | 58.6 | 0.72 | 50 | 39.6 | 50.1 | 0 | 50.7 | 10.4 | 215.9 | 10.4 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 49-000087
TR_B (available) | 50-007380
TR_A Rated kVA | 100
TR_B Rated kVA | 160
TR_A Baseline Loading% | 39.6
TR_B Baseline Loading% | 50.1
Total Scenarios Evaluated | 48
Feasible Scenarios | 16
--- Optimal Solution ---
Switch Parent Node | 48
Switch Child Node | 47
Tie Node (TR_A side) | 42
Tie Node (TR_B side) | 42
Tie Line Distance (m) | 33
Load Transferred (kW) | 2.37
TR_A Loading After (%) | 39.6
TR_B Loading After (%) | 51.9
Minimum Voltage (V) | 215.9