## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 24 | 25 | 88 | 34 | 47.5 | 11.83 | 50 | 85 | 43.4 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 25 | 88 | 88 | 34 | 47.5 | 11.83 | 50 | 85 | 43.4 | 71.2 | 58.3 | 218.6 | 205.4 | 205.4 | NO
| NG | 88 | 20 | 20 | 34 | 47.5 | 11.83 | 50 | 85 | 43.4 | 71.2 | 58.3 | 218.6 | 205.6 | 205.6 | NO
| NG | 0 | 1 | 1 | 6 | 82.3 | 16.78 | 50 | 85 | 43.4 | 0 | 64.5 | 10.5 | 201.1 | 10.5 | NO
1 | OK | 0 | 10 | 75 | 25 | 72.7 | 6.7 | 50 | 85 | 43.4 | 77.1 | 51.2 | 217.5 | 216.4 | 216.4 | YES
| NG | 1 | 11 | 11 | 6 | 106 | 15.46 | 50 | 85 | 43.4 | 66.8 | 63 | 216.3 | 200.7 | 200.7 | NO
| NG | 4 | 5 | 5 | 6 | 77.2 | 36.03 | 50 | 85 | 43.4 | 42.5 | 88.1 | 223.6 | 208.2 | 208.2 | NO
2 | OK | 11 | 85 | 85 | 6 | 115.1 | 6.04 | 50 | 85 | 43.4 | 75.4 | 50.7 | 216.7 | 214.4 | 214.4 | YES
| NG | 5 | 6 | 7 | 27 | 78.6 | 33.47 | 50 | 85 | 43.4 | 45.5 | 85 | 223.3 | 208 | 208 | NO
3 | OK | 6 | 7 | 7 | 27 | 78.6 | 23.37 | 50 | 85 | 43.4 | 57.2 | 71.9 | 221.9 | 211.8 | 211.8 | YES
4 | OK | 6 | 97 | 97 | 27 | 98.3 | 9.78 | 50 | 85 | 43.4 | 73.3 | 55.1 | 216.7 | 214.9 | 214.9 | YES
5 | OK | 7 | 8 | 12 | 34 | 79 | 16.88 | 50 | 85 | 43.4 | 64.8 | 63.7 | 221.4 | 214.9 | 214.9 | YES
6 | OK | 7 | 47 | 47 | 27 | 83.3 | 6.49 | 50 | 85 | 43.4 | 77.2 | 51 | 217.7 | 216 | 216 | YES
7 | OK | 97 | 83 | 83 | 27 | 105.5 | 9.06 | 50 | 85 | 43.4 | 74.2 | 54.2 | 216.3 | 214.9 | 214.9 | YES
8 | OK | 8 | 9 | 12 | 34 | 79 | 12.32 | 50 | 85 | 43.4 | 70.2 | 58.1 | 220.7 | 215.8 | 215.8 | YES
9 | OK | 47 | 48 | 48 | 27 | 89.1 | 6.49 | 50 | 85 | 43.4 | 77.2 | 50.4 | 217.8 | 215.9 | 215.9 | YES
10 | OK | 83 | 81 | 81 | 27 | 108.7 | 9.06 | 50 | 85 | 43.4 | 74.2 | 54.2 | 216.3 | 214.9 | 214.9 | YES
11 | OK | 9 | 12 | 12 | 34 | 79 | 12.32 | 50 | 85 | 43.4 | 70.2 | 58.1 | 220.7 | 215.8 | 215.8 | YES
12 | OK | 48 | 49 | 49 | 27 | 92.3 | 5.83 | 50 | 85 | 43.4 | 78 | 50.2 | 217.3 | 216 | 216 | YES
13 | OK | 81 | 82 | 82 | 6 | 112.2 | 8.56 | 50 | 85 | 43.4 | 74.8 | 53.6 | 216.3 | 214.9 | 214.9 | YES
14 | OK | 12 | 58 | 58 | 34 | 89.9 | 10.36 | 50 | 85 | 43.4 | 72.5 | 55.8 | 220.3 | 215.8 | 215.8 | YES
15 | OK | 49 | 50 | 50 | 27 | 94.4 | 5.83 | 50 | 85 | 43.4 | 78 | 50.2 | 217.3 | 216 | 216 | YES
16 | OK | 82 | 45 | 45 | 6 | 117.1 | 7.25 | 50 | 85 | 43.4 | 76.3 | 52 | 216.4 | 215.6 | 215.6 | YES
17 | OK | 58 | 68 | 68 | 34 | 92.2 | 9.93 | 50 | 85 | 43.4 | 73.1 | 55.3 | 220.2 | 215.6 | 215.6 | YES
18 | OK | 45 | 46 | 46 | 6 | 120.4 | 6.22 | 50 | 85 | 43.4 | 77.5 | 50.7 | 216.4 | 215.6 | 215.6 | YES
19 | OK | 68 | 13 | 13 | 34 | 95.8 | 8.54 | 50 | 85 | 43.4 | 74.7 | 53.5 | 220.2 | 216.3 | 216.3 | YES
20 | OK | 46 | 78 | 78 | 6 | 129.7 | 6.22 | 50 | 85 | 43.4 | 77.5 | 50.7 | 216.4 | 215.6 | 215.6 | YES
21 | OK | 13 | 14 | 14 | 34 | 99.7 | 8.48 | 50 | 85 | 43.4 | 74.8 | 53.5 | 220.1 | 216.4 | 216.4 | YES
22 | OK | 78 | 72 | 72 | 6 | 132.8 | 5.18 | 50 | 85 | 43.4 | 78.8 | 49.5 | 215.8 | 215.5 | 215.5 | YES
23 | OK | 14 | 59 | 59 | 34 | 103.9 | 8.48 | 50 | 85 | 43.4 | 74.8 | 53.5 | 220.1 | 216.4 | 216.4 | YES
24 | OK | 59 | 60 | 60 | 34 | 106.3 | 8.48 | 50 | 85 | 43.4 | 74.8 | 53.5 | 220.1 | 216.4 | 216.4 | YES
25 | OK | 60 | 66 | 66 | 34 | 109.9 | 8.48 | 50 | 85 | 43.4 | 74.8 | 53.5 | 220.1 | 216.4 | 216.4 | YES
26 | OK | 66 | 15 | 15 | 34 | 112.3 | 8.46 | 50 | 85 | 43.4 | 74.8 | 53.4 | 220.2 | 216.4 | 216.4 | YES
27 | ** OPTIMAL ** | 15 | 16 | 16 | 34 | 117 | 8.16 | 50 | 85 | 43.4 | 75.2 | 53.1 | 220 | 216.5 | 216.5 | YES
| NG | 16 | 17 | 17 | 34 | 122.5 | 8.16 | 50 | 85 | 43.4 | 75.2 | 51.6 | 220 | 11.3 | 11.3 | NO
28 | OK | 17 | 67 | 67 | 34 | 130.7 | 5.72 | 50 | 85 | 43.4 | 78.1 | 50.1 | 219.8 | 216.4 | 216.4 | YES
29 | OK | 67 | 69 | 69 | 34 | 139.4 | 5.34 | 50 | 85 | 43.4 | 78.5 | 49.7 | 219.8 | 216.4 | 216.4 | YES
30 | OK | 69 | 63 | 63 | 34 | 150.7 | 5.02 | 50 | 85 | 43.4 | 78.9 | 49.3 | 219.4 | 216.4 | 216.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 49-006945
TR_B (available) | 48-009349
TR_A Rated kVA | 100
TR_B Rated kVA | 100
TR_A Baseline Loading% | 85
TR_B Baseline Loading% | 43.4
Total Scenarios Evaluated | 38
Feasible Scenarios | 30
--- Optimal Solution ---
Switch Parent Node | 15
Switch Child Node | 16
Tie Node (TR_A side) | 16
Tie Node (TR_B side) | 34
Tie Line Distance (m) | 117
Load Transferred (kW) | 8.16
TR_A Loading After (%) | 75.2
TR_B Loading After (%) | 53.1
Minimum Voltage (V) | 216.5